## 2020
Circuit | Date of outage | Cause of outage | Conductor type | Type of equipment | Outage duration (min) | Total number of customers impacted
Harnish | 2020-02-15 | Equipment Failure - Transformer | overhead (OH) bare conductor | Transformer | 80 | 98
Harnish | 2020-02-15 | Same outage as above | overhead (OH) bare conductor | Same Outage as above | 240 | 2
Harnish | 2020-02-15 | Same outage as above | overhead (OH) bare conductor | Same Outage as above | 510 | 1
Paradise | 2020-06-28 | Failed fuse cutout to service transformer | overhead (OH) bare conductor | Fuse | 97 | 20
Georgia | 2020-07-30 | Failed fuse cutout to service transformer | overhead (OH) bare conductor | Fuse | 85 | 19
Baldwin | 2020-09-14 | 34kV Riser connector failed | Connector | Connector | 33 | 9512
Shay | 2020-09-14 | Same Outage as above | Connector | Same Outage as above | 34 | 14823
Goldmine | 2020-09-14 | Same Outage as above | Connector | Same Outage as above | 468 | 1984
Harnish | 2020-09-14 | Same Outage as above | Connector | Same Outage as above | 216 | 254
Lagonita | 2020-09-14 | Same Outage as above | Connector | Same Outage as above | 249 | 1103
Boulder | 2020-09-14 | Same Outage as above | Connector | Same Outage as above | 201 | 2046
Boulder | 2020-09-14 | Same Outage as above | Connector | Same Outage as above | 18 | 1373
Boulder | 2020-09-14 | Same Outage as above | Connector | Same Outage as above | 22 | 410
Pioneer | 2020-12-10 | TripSaver opened. (Trip Saver replaced with ELF. Measured 3.6 amps on line when ELF installed. Suspect TripSaver defective.) | overhead (OH) bare conductor | Tripsaver fuse | 8 | 60
Georgia | 2020-12-19 | Fuse holder would not hold an ELF properly and openned. Changed out fuse holder. | overhead (OH) bare conductor | Fuse holder | 9 | 51
Georgia | 2020-12-20 | Fuse holder would not hold an ELF properly and openned. Changed out fuse holder. | overhead (OH) bare conductor | Fuse holder | 14 | 89
Shay | 2020-12-27 | UG to OH connector failed. | Connector | Connector | 11420 | 115

## 2021
Circuit | Date of outage | Cause of outage | Conductor type | Type of equipment | Outage duration (min) | Total number of customers impacted
Harnish | 2021-01-02 | Failed UG cable. | underground (UG) cable | Conductor failure | 120 | 254
Lagonita | 2021-01-02 | Same outage as above | underground (UG) cable | Same outage as above | 55 | 1103
North Shore | 2021-01-22 | Failed tree attachment. | Service line | Conductor failure | 347 | 1
Sunrise | 2021-07-09 | Transformer failed | overhead (OH) bare conductor | Transformer | 161 | 12
Erwin Lake | 2021-08-10 | Secondaries in pad made contact causing TripSaver to open | underground (UG) cable | Conductor failure | 6 | 39
Holdcomb | 2021-09-03 | Transfonrmer 34kV feed into Bear City Sub failed | underground (UG) cable | Connector | 44 | 1587
Georgia | 2021-10-25 | TripSaver opened, reason unknown | overhead (OH) bare conductor | Tripsaver fuse | 91 | 200
Clubview | 2021-10-25 | Failed transformer | overhead (OH) bare conductor | Transformer | 82 | 20
Sunset | 2021-10-26 | Failed Transformer | overhead (OH) bare conductor | Transformer | 77 | 15

## 2022
Circuit | Date of outage | Cause of outage | Conductor type | Type of equipment | Outage duration (min) | Total number of customers impacted
Interlaken | 2022-08-25 | Primary U.G. #4 str. Cu in C.I.C. failed. Two runs of new cable were abled to be installed (160'). | underground (UG) cable | Conductor failure | 1832 | 50
Clubview | 2022-09-12 | 10 kVA transformer failed. Installed a new 50kVA XFMR | overhead (OH) bare conductor | Transformer | 166 | 8
Boulder | 2022-12-10 | Failed 15kVA transformer | overhead (OH) bare conductor | Transformer | 205 | 17