## a
Type | Outage Date | Cause Category | Description of Cause
Unplanned | 2023-01-09 | Contact - Vegetation Weather | Tree came down and broke the #2 str. H.T. that feeds St. Cloud
Unplanned | 2023-01-10 | Contact - Vegetation Weather | High winds blew tree down
Unplanned | 2023-01-10 | Contact - Vegetation Weather | High Winds caused vegetation to hit the lines.
Unplanned | 2023-01-10 | Equipment Failure - TripSaver | TripSaver opened cause unknown
Unplanned | 2023-01-19 | Equipment Failure - Connector | Bad primary connection at cut-out, high side of XFMR
Unplanned | 2023-01-21 | Equipment Failure - Fuse Holder | blown 6 amp ELF
Unplanned | 2023-01-22 | Equipment Failure - Other | bad 5kVA XFMR/open trip saver
Unplanned | 2023-02-14 | Equipment Failure - Conuctor Failure | Neutral broke off XFMR gnd. Due to wind
Unplanned | 2023-02-21 | Contact - Wire to wire slap | wind slapped together primary phases wind from storm
Unplanned | 2023-02-21 | Contact - Vegetation Weather | Wind event caused down tree, primary broke
Unplanned | 2023-02-22 | Contact - Vegetation Weather | Tree fell taking down service and secondary, Snow & wind
Unplanned | 2023-04-18 | Contact - Other | Crew went phase to phase while transferring conductor
Unplanned | 2023-05-05 | Overload - Other | blown 18 amp elf fuse
Unplanned | 2023-06-19 | Loss of Supply - SCE | SCE 34kV Doble & Cushenbury lines relayed and did not test, Fault in SCE's Goldhill Substation
Unplanned | 2023-07-01 | Equipment Failure - TripSaver | TripSaver on pole 5630BV went bad: code ! 0
Unplanned | 2023-07-09 | Third Party - Car Hit Pole/Guy | Car hit guy wire and cracked the pole. Also broke a 34kV cross arm 2 spans away.
Unplanned | 2023-07-12 | Other | Contractor had a planned outage and the crew forgot to hook up one XFMR primary lead
Unplanned | 2023-07-22 | Equipment Failure - Other | PS3436IR opened on imbalance (ground) sensing equipment bad
Unplanned | 2023-08-13 | Overload - Lightening | 25kVA XFMR ELF blew at 565 Crestwood
Unplanned | 2023-08-13 | Overload - Lightening | 15kVA XFMR ELF blew
Unplanned | 2023-08-13 | Overload - Lightening | 15kVA XFMR ELF blew
Unplanned | 2023-08-30 | Third Party - Other | Outsource crew contacted phase Interlaken servicing Goldmine and portion of Club View circuits
Unplanned | 2023-09-12 | Unknown | Could not find a problem, Amps were low 12 to 24. (Suspected customer problem when installing a generator.)
Unplanned | 2023-09-16 | Contact - Animal | A hawk contacted the Baldwin 34kV line at Fawnskin Sub. No damage
Unplanned | 2023-09-21 | Equipment Failure - TripSaver | TS963 at c/o Pinewood & Ridgeside Dr opened. Fault on TS. Could not find anything wrong with the primary.
Unplanned | 2023-11-12 | Unknown | trip saver opened on 0 amp fault and had 13 amps when reclosed
Unplanned | 2023-11-16 | Contact - Other | Outsource contacted phases
Unplanned | 2023-11-17 | Unknown | open trip saver 0 fault amps
Unplanned | 2023-11-19 | Contact - Vehicle | car v/s pole CHP report # 9865
Unplanned | 2023-12-20 | Loss of Supply - SCE | SCE Lugo reported a CB at SCE's Goldhill Substation opened. This de-energized BVES' 34kV Baldwin & Shay Lines. SCE to investigate
Unplanned | 2023-12-21 | Equipment Failure - TripSaver | TripSaver opened cause unknown
Unplanned | 2023-12-22 | Equipment Failure - TripSaver | TripSaver opened on 0 amps (fault) had 23 amps on it
Unplanned | 2023-12-22 | Equipment Failure - Other | 34kV Radford IR3470 opened reason unknown. Switch over to Shay Line did not switch on it's own
Unplanned | 2023-12-23 | Equipment Failure - TripSaver | TripSaver opened on 0 amps (fault) had 13 amps on it
Unplanned | 2023-12-25 | Equipment Failure - Connector | possible bad connector on PD1122 on 13739BV Big Bear Blvd / Barranca
Unplanned | 2023-12-27 | Equipment Failure - TripSaver | TripSaver opened on 0 amp (fault) had 14 amps on it
Unplanned | 2023-12-27 | Equipment Failure - Other | Blown 6 amp ELF fuse. 10kVA XFMR 6 amp elf fuse blown replaced w/12 amp fuse
Unplanned | 2023-12-29 | Equipment Failure - TripSaver | TripSaver opened on 0 amps (fault) had 16 amps on it
Unplanned | 2024-01-11 | Equipment Failure - Other | bad fuse on XFMR
Unplanned | 2024-01-20 | Overload - Loading | Overloaded 5kVA XFMR replaced with a 25kVA XFMR
Unplanned | 2024-02-06 | Contact - Vegetation Weather | Tree came down on wire, snow storm
Unplanned | 2024-02-06 | Equipment Failure - Conuctor Failure | Primary Down due to snow storm
Unplanned | 2024-02-06 | Contact - Vegetation Weather | Tree down on Primary due to snow storm
Unplanned | 2024-02-06 | Equipment Failure - Conuctor Failure | Primary Down due to snow storm
Unplanned | 2024-02-06 | Equipment Failure - Conuctor Failure | Snow storm, wire down
Unplanned | 2024-02-06 | Loss of Supply - SCE | SCE Vista, Sanderson reports 33kV Bear Valley Line relayed and did not test
Unplanned | 2024-02-07 | Contact - Vegetation Weather | tree fell thru power lines tree opened AR105
Unplanned | 2024-02-07 | Contact - Vegetation Weather | open neutral in span due to tree branch falling during storm
Unplanned | 2024-03-09 | Loss of Supply - SCE | SCE Lugo reports a 115kV wire down plus setting issue at Goldhill
Unplanned | 2024-03-14 | Contact - Vegetation Weather | Tree fell on lines
Unplanned | 2024-03-16 | Third Party - Car Hit Pole/Guy | Car Hit Pole
Unplanned | 2024-03-25 | Contact - Wire to wire slap | Outsource slapped wires together-AR805 tripped-composite cross arm broken
Unplanned | 2024-03-28 | Contact - Wire to wire slap | Outsource had a phase slipped out of a grip and contacted the secondary relaying the circuit slapped wires together-AR805 tripped-composite cross arm broken
Unplanned | 2024-03-31 | Contact - Vegetation Weather | Primary Neutral wire down. Opened TripSaver to make repairs
Unplanned | 2004-04-29 | Unknown | Location unknown, patrolled 4kV Northshore and could not find a cause. Outsource was replacing a pole near North Shore Dr. x Bear Loop. They deny causing the outage. 4C Panel showed phase to ground fault: Ø=3,700 amps & ground 3,600 amps
Unplanned | 2024-06-03 | Equipment Failure - Fuse Holder | a porcelin cut-out broke on pole BV11386. The 18 amp fuse was still good, it just fell open due to the broken cut-out
Unplanned | 2024-06-09 | Other | House fire caused TripSaver to open
Unplanned | 2024-06-18 | Operator Error | Loading Engineering settings in 4kV Boulder CB100 Form 6 panel, CB tripped (settings mis-match) by Engineering
Unplanned | 2024-06-25 | Equipment Failure - AR/Switch | Cold Load pck up - 4kV Garstin CB600 tripped
Unplanned | 2024-07-08 | Contact - Wire to wire slap | Object on wire caused phase to slap
Unplanned | 2024-08-13 | Equipment Failure - Fuse Holder | porcelain 100 amp cut-out broke in half
Unplanned | 8/26/202 | Equipment Failure - Other | When closing fuses on a 750kVA XFMR AR632 opened. Reverse feed thru the AR due to circuit configuration. Castle Glen circuit servicing load (normally Interlaken circuit).
Unplanned | 2024-10-01 | Equipment Failure - Other | Broken hendrix insulator, conductor was floating, climbed pole to make repairs, de-energized due to location is heavily wood
Unplanned | 2024-10-16 | Contact - Vehicle | BV Paving crew member ran into D.G. with equipment causing TS626 to open, TS625 on same pole remained closed
Unplanned | 2024-10-31 | Equipment Failure - Other | 34kV Switzerland PS3469IR pole #2 (middle) blew up. 44,832 AMPS at trip. Moonridge's 4kV Clubview & Goldmine plus Bear Mountain's 4kV Geronimo circuits off
Unplanned | 2024-11-14 | Contact - Balloon | Mylar Ballon went into primary and locked out circuit (AR145)
Unplanned | 2024-12-05 | Third Party - Car Hit Pole/Guy | Car hit pole, needed to replace pole from damage.
Unplanned | 2024-12-06 | Equipment Failure - Transformer | broken secondary bushing on a 10KVA XFMR.
Unplanned | 2024-12-14 | Equipment Failure - TripSaver | TripSaver opened after Radford switchover

## b
Momentary/Sustained | Type | Outage Number | Outage Date | Circuit | Substation | Location (Street Address) | Area | Number of Customers Out | Outage Duration | Customer Minutes Out | Event SAIDI | Daily SAIDI | TMED Exceeded | Cause Category | Wire Down | Protective Device Actuated | Description of Cause | Work Order | GO 166 Report | Fire Risk Rating | Red Flag Warning Day | High Wind Warning Day | HFTD Tier | Wildfire Near Miss | Additional Comments
S | Unplanned |  | 2023-01-09 | Erwin Lake | Maltby Substation | 416 San Martin | Sugarloaf | 5 | 96 | 480 | 0.019653 | 0.019653 | No | Contact - Vegetation Weather | Yes | ELF Blown | Tree came down and broke the #2 str. H.T. that feeds St. Cloud |  | No | Green | No | Yes | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-01-10 | Boulder | Village Substation | 39771 Forest | Big Bear Lake | 8 | 120 | 960 | 0.039306 | 3.277 | No | Contact - Vegetation Weather | Yes | No | High winds blew tree down |  | No | Green | No | Yes | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-01-10 | North Shore | Fawnskin Substation | 40006 North Shore | Fawnskin | 1523 | 49 | 74627 | 3.0555 |  | No | Contact - Vegetation Weather | No | AR/Switch Actuated | High Winds |  | No | Green | No | Yes | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-01-10 | Boulder | Village Substation | 749 Cienega | Big Bear Lake | 50 | 89 | 4450 | 0.1822 |  | No | Equipment Failure - TripSaver | No | TripSaver Actuated | TripSaver opened cause unknown |  | No | Green | No | Yes | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-01-19 | Erwin Lake | Maltby Substation | 357 Greenspot | Big Bear City | 11 | 247 | 2717 | 0.11124 | 0.11124 | No | Equipment Failure - Connector | No | No | Bad primary connection at cut-out, high side of XFMR |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-01-21 | Sunrise | Maple Substation | 190 Victoria Ln | Sugarloaf | 8 | 150 | 1200 | 0.049132 | 0.049132 | No | Equipment Failure - Fuse Holder | No | ELF Blown | blown 6 amp ELF |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-01-22 | North Shore | Fawnskin Substation | BB track lease #311 | Fawnskin | 3 | 347 | 1041 | 0.042622 | 0.042622 | No | Equipment Failure - Other | No | TripSaver Actuated | bad 5kVA XFMR/open trip saver |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-02-14 | Pioneer | Palomino Substation | 454040 3rd | Big Bear City | 3 | 113 | 339 | 0.01388 | 0.01388 | No | Equipment Failure - Conuctor Failure | No | No | Neutral broke off XFMR gnd. Due to wind |  | No | Green | No | Yes | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-02-21 | Sunset | Maple Substation | 600 block of Orange s/o Barton | Sugarloaf | 1629 | 180 | 293220 | 12.0054 | 18.9315 | No | Contact - Wire to wire slap | No | AR/Switch Actuated | wind slapped together primary phases wind from storm | 60400135 | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-02-21 | North Shore | Fawnskin Substation | Rim of the World 1/4 mile beyond pavement | Fawnskin | 1353 | 120 | 162360 | 6.6476 |  | No | Contact - Vegetation Weather | Yes | AR/Switch Actuated | Wind event caused down tree, primary broke | 60400135 | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-02-21 | North Shore | Fawnskin Substation | Rim of the World 1/4 mile beyond pavement | Fawnskin | 12 | 567 | 6804 | 0.27858 |  | No | Contact - Vegetation Weather |  |  | Same outage as above | 60400135 | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-02-22 | Paradise | Maltby Substation | 437 Sugarloaf | Big Bear City | 4 | 118 | 472 | 0.019325 | 0.019325 | No | Contact - Vegetation Weather | Yes | No | Tree fell taking down service and secondary, Snow & wind |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-04-18 | Erwin Lake | Maltby Substation | Woodland x 7th | Erwin Lake | 2015 | 60 | 120900 | 4.95 | 4.8957 | No | Contact - Other | No | AR/Switch Actuated | Crew went phase to phase while transferring conductor | 60400131 | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-05-05 | Erwin Lake | Maltby Substation | 2129 1st Ln | Erwin Lake | 14 | 92 | 1288 | 0.052735 | 0.052156 | No | Overload - Other | No | ELF Blown | blown 18 amp elf fuse |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-06-19 | Baldwin | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear City | 6802 | 108 | 734616 | 30.0776 | 126.9049 | Yes | Loss of Supply - SCE | No | AR/Switch Actuated | SCE 34kV Doble & Cushenbury lines relayed and did not test, Fault in SCE's Goldhill Substation |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-06-19 | Baldwin | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear City | 4907 | 2 | 9814 | 0.40182 |  | Yes | Loss of Supply - SCE |  |  | Same outage as above |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-06-19 | Baldwin | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear City | 4 | 10 | 40 | 0.0016377 |  | Yes | Loss of Supply - SCE |  |  | Same outage as above |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-06-19 | Shay | SCE Goldhill Substation | 34kV Shay IR3440 | Big Bear Lake | 7644 | 184 | 1406496 | 57.5866 |  | Yes | Loss of Supply - SCE |  |  | Same outage as above |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-06-19 | Garstin | SCE Goldhill Substation | 34kV Shay IR3440 | Big Bear Lake | 1056 | 111 | 117216 | 4.7992 |  | Yes | Loss of Supply - SCE |  |  | Same outage as above |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-06-19 | Garstin | SCE Goldhill Substation | 34kV Shay IR3440 | Big Bear Lake | 1040 | 17 | 17680 | 0.72388 |  | Yes | Loss of Supply - SCE |  |  | Same outage as above |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-06-19 | Garstin | SCE Goldhill Substation | 34kV Shay IR3440 | Big Bear Lake | 1020 | 44 | 44880 | 1.8375 |  | Yes | Loss of Supply - SCE |  |  | Same outage as above |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-06-19 | Garstin | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear Lake | 1056 | 9 | 9504 | 0.38913 |  | Yes | Loss of Supply - SCE |  |  | Same outage as above |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-06-19 | Interlaken | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear Lake | 880 | 120 | 105600 | 4.3236 |  | Yes | Loss of Supply - SCE |  |  | Same outage as above |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-06-19 | Interlaken | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear Lake | 850 | 4 | 3400 | 0.13921 |  | Yes | Loss of Supply - SCE |  |  | Same outage as above |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-06-19 | Interlaken | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear Lake | 840 | 8 | 6720 | 0.27514 |  | Yes | Loss of Supply - SCE |  |  | Same outage as above |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-06-19 | Interlaken | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear Lake | 810 | 18 | 14580 | 0.59695 |  | Yes | Loss of Supply - SCE |  |  | Same outage as above |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-06-19 | Interlaken | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear Lake | 800 | 22 | 17600 | 0.7206 |  | Yes | Loss of Supply - SCE |  |  | Same outage as above |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-06-19 | Interlaken | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear Lake | 880 | 9 | 7920 | 0.32427 |  | Yes | Loss of Supply - SCE |  |  | Same outage as above |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-06-19 | Interlaken | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear Lake | 100 | 145 | 14500 | 0.59368 |  | Yes | Loss of Supply - SCE |  |  | Same outage as above |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-06-19 | Fox Farm | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear Lake | 35 | 182 | 6370 | 0.26081 |  | Yes | Loss of Supply - SCE |  |  | Same outage as above |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-06-19 | Erwin Lake | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear City | 2533 | 230 | 582590 | 23.8532 |  | Yes | Loss of Supply - SCE |  |  | Same outage as above |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-07-01 | Eagle | Pineknot Substation | s/e corner Finch x Swallow | Big Bear Lake | 50 | 53 | 2650 | 0.1085 | 0.1085 | No | Equipment Failure - TripSaver | No | TripSaver Actuated | TripSaver on pole 5630BV went bad: code ! 0 |  | No | Yellow | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-07-09 | Shay | Moonridge Substation | 896 Clubview Dr | Big Bear Lake | 15000 | 61 | 915000 | 37.4632 | 98.6079 | Yes | Third Party - Car Hit Pole/Guy | No | AR/Switch Actuated | Car hit guy wire and cracked the pole. Also broke a 34kV cross arm 2 spans away. |  | No | Yellow | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-07-09 | Shay | Moonridge Substation | 896 Clubview Dr | Big Bear Lake | 3800 | 393 | 1493400 | 61.1448 |  | Yes | Third Party - Car Hit Pole/Guy |  |  | Same outage as above |  | No | Yellow | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-07-12 | Erwin Lake | Maltby Substation | C ln x Juniper | Erwin Lake | 18 | 120 | 2160 | 0.088438 | 0.1474 | No | Other | No | Other | Outsource had a planned outage and the crew forgot to hook up one XFMR primary lead |  | No | Yellow | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-07-12 | Erwin Lake | Maltby Substation | Oak x D ln | Erwin Lake | 16 | 90 | 1440 | 0.058958 |  | No | Other |  |  | Same outage as above |  | No | Yellow | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-07-22 | Shay |  | PS3436IR Shay w/o Barranca | Service Area Wide | 16599 | 89 | 1477311 | 60.486 | 60.486 | Yes | Equipment Failure - Other | No | AR/Switch Actuated | PS3436IR opened on imbalance (ground) sensing equipment bad |  | Yes | Brown | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-08-13 | Garstin | Meadow Substation | 562 Ponderosa x Brownie | Big Bear Lake | 8 | 83 | 664 | 0.027186 | 0.068785 | No | Overload - Lightening | No | ELF Blown | 25kVA XFMR ELF blew at 565 Crestwood |  | No | Yellow | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-08-13 | Castle Glen | Division Substation | 1209 Juniper | Big Bear City | 11 | 74 | 814 | 0.033328 |  | No | Overload - Lightening | No | ELF Blown | 15kVA XFMR ELF blew |  | No | Yellow | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-08-13 | Castle Glen | Division Substation | 626 McAlister | Big Bear City | 2 | 101 | 202 | 0.0082706 |  | No | Overload - Lightening | No | ELF Blown | 15kVA XFMR ELF blew |  | No | Yellow | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-08-30 | Interlaken | Meadow Substation | Club View Dr | Big Bear Lake | 3014 | 61 | 183854 | 7.5276 | 7.6504 | No | Third Party - Other | No | AR/Switch Actuated | Outsource crew contacted phase Interlaken servicing Goldmine and portion of Club View circuits |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-08-30 | Interlaken | Meadow Substation | Club View Dr | Big Bear Lake | 150 | 20 | 3000 | 0.12283 |  | No | Third Party - Other |  |  | Same outage as above |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-09-12 | North Shore | Fawnskin Substation | 1023 Fawnskin Dr | Fawnskin | 8 | 90 | 720 | 0.029479 | 0.029479 | No | Unknown | No | ELF Blown | Could not find a problem, Amps were low 12 to 24. (Suspected customer problem when installing a generator.) |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-09-16 | Baldwin | Fawnskin Substation | Fawnskin Substation | Big Bear City | 8700 | 58 | 504600 | 20.66 | 22.3925 | No | Contact - Animal | No | AR/Switch Actuated | A hawk contacted the Baldwin 34kV line at Fawnskin Sub. No damage |  | No | Green | No | No | 2 | No | Possible spark producing event from hawk striking line, however no vegetation nearby.
S | Unplanned |  | 2023-09-16 | Baldwin | Fawnskin Substation | Fawnskin Substation | Big Bear City | 2015 | 21 | 42315 | 1.7325 |  | No |  |  |  | Same outage as above |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-09-21 | Castle Glen | Division Substation | 1161 Sugarpine Dr | Big Bear City | 14 | 51 | 714 | 0.029234 | 0.029234 | No | Equipment Failure - TripSaver | No | TripSaver Actuated | TS963 at c/o Pinewood & Ridgeside Dr opened. Fault on TS. Could not find anything wrong with the primary. |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-11-12 | Erwin Lake | Maltby Substation | Malabar/Zaca | Big Bear City | 25 | 63 | 1575 | 0.064486 | 0.063778 | No | Unknown | No | TripSaver Actuated | trip saver opened on 0 amp fault and had 13 amps when reclosed |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-11-16 | Goldmine | Moonridge Substation | Wolf x Villa Grove | Big Bear Lake | 2660 | 25 | 66500 | 2.7227 | 4.5496 | No | Contact - Other | No | AR/Switch Actuated | Outsource contacted phases |  | No | Green | No | No | 2 | No | Possible Spark producing event. However, no vegetation in area and the AR actuated.
S | Unplanned |  | 2023-11-16 | Goldmine | Moonridge Substation | Wolf x Villa Grove | Big Bear Lake | 2000 | 13 | 26000 | 1.0645 |  | No | Contact - Other |  |  | Same outage as above |  | No | Green | No | No | 2 | No
S | Unplanned |  | 2023-11-16 | Goldmine | Moonridge Substation | Wolf x Villa Grove | Big Bear Lake | 2660 | 7 | 18620 | 0.76236 |  | No | Contact - Other |  |  | Same outage as above |  | No | Green | No | No | 2 | No
S | Unplanned |  | 2023-11-17 | Goldmine | Moonridge Substation | 828 Tehama | Big Bear Lake | 30 | 137 | 4110 | 0.16828 | 0.16643 | No | Unknown | No | TripSaver Actuated | open trip saver 0 fault amps |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-11-19 | Baldwin |  | 2 spans e/o Bear Loop | Big Bear Lake | 11621 | 72 | 836712 | 34.2578 | 37.7584 | No | Contact - Vehicle | Yes | AR/Switch Actuated | car v/s pole CHP report # 9865 |  | No | Green | No | Yes | 2 | No | Possible spark producing event; however wildfire risk low due to high moisture and low fuel in area. Tripsaver may have tripped before spark production.
S | Unplanned |  | 2023-11-19 | Baldwin |  | 2 spans e/o Bear Loop | Big Bear Lake | 75 | 1140 | 85500 | 3.5007 |  | No | Contact - Vehicle |  |  | Same outage as above |  | No | Green | No | Yes | 2 | No
M | Unplanned |  | 2023-12-20 | SCE Goldhill Ute Lines | SCE Goldhill Substation | SCE Goldhill Substation | Service Area Wide | 21203 | 4 | 84812 | 3.4725 | 3.4725 | No | Loss of Supply - SCE | No | No | SCE Lugo reported a CB at SCE's Goldhill Substation opened. This de-energized BVES' 34kV Baldwin & Shay Lines. SCE to investigate |  | No | Green | No | Yes | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-12-21 | Clubview | Moonridge Substation | 42736 Sonoma | Big Bear Lake | 50 | 78 | 3900 | 0.15968 | 0.15968 | No | Equipment Failure - TripSaver | No | TripSaver Actuated | TripSaver opened cause unknown |  | No | Green | No | Yes | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-12-22 | Goldmine | Moonridge Substation | Primrose x Primrose Ct. Pole 3566BV | Big Bear Lake | 30 | 140 | 4200 | 0.17196 | 7.2081 | No | Equipment Failure - TripSaver | No | TripSaver Actuated | TripSaver opened on 0 amps (fault) had 23 amps on it |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-12-22 |  | Village Substation | Village Substation: 4kV Bouder, Harnish & Lagunita circuits | Big Bear Lake | 3437 | 50 | 171850 | 7.0361 |  | No | Equipment Failure - Other | No | AR/Switch Actuated | 34kV Radford IR3470 opened reason unknown. Switch over to Shay Line did not switch on it's own |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-12-23 |  | Village Substation | Village Substation: 4kV Bouder, Harnish & Lagunita circuits | Big Bear Lake | 2046 | 31 | 63426 | 2.5969 | 2.6629 | No | Equipment Failure - Other |  |  | Same outage as above |  | No | Green | No | No | 2 | No
S | Unplanned |  | 2023-12-23 | Clubview | Moonridge Substation | 42935 Dogwood | Big Bear Lake | 13 | 124 | 1612 | 0.066001 |  | No | Equipment Failure - TripSaver | No | TripSaver Actuated | TripSaver opened on 0 amps (fault) had 13 amps on it |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-12-25 | Erwin Lake | Maltby Substation | 1208 Big Bear Bl. | Big Bear City | 1000 | 121 | 121000 | 4.9541 | 4.9541 | No | Equipment Failure - Connector | No | AR/Switch Actuated | possible bad connector on PD1122 on 13739BV Big Bear Blvd / Barranca |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-12-27 | North Shore | Fawnskin Substation | 42402 Golden Oak | Big Bear Lake | 100 | 59 | 5900 | 0.24157 | 0.41783 | No | Equipment Failure - TripSaver | No | TripSaver Actuated | TripSaver opened on 0 amp (fault) had 14 amps on it |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-12-27 | Interlaken | Meadow Substation | 200 N Teakwood | Big Bear Lake | 50 | 75 | 3750 | 0.15354 |  | No | Equipment Failure - TripSaver |  |  | Same outage as above |  | No | Green | No | No | 2 | No
S | Unplanned |  | 2023-12-27 | Sunrise | Maple Substation | 240 Los Angeles | Sugarloaf | 15 | 37 | 555 | 0.022724 |  | No | Equipment Failure - Other | No | ELF Blown | Blown 6 amp ELF fuse. 10kVA XFMR 6 amp elf fuse blown replaced w/12 amp fuse |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2023-12-29 | Castle Glen | Division Substation | corner of Grove x Division | Big Bear Lake | 25 | 90 | 2250 | 0.092123 | 0.092123 | No | Equipment Failure - TripSaver | No | TripSaver Actuated | TripSaver opened on 0 amps (fault) had 16 amps on it |  | No | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-01-11 | North Shore | Fawnskin Substation | 38740 Northshore Dr | Fawnskin | 7 | 230 | 1610 | 0.065919 | 0.065919 | No | Equipment Failure - Other | No | ELF Blown | bad fuse on XFMR | 60400218 |  | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-01-20 | Sunrise | Maple Substation | 214 Victoria Ln | Sugarloaf | 12 | 156 | 1872 | 0.076646 | 0.076646 | No | Overload - Loading | No | Other | Overloaded 5kVA XFMR replaced with a 25kVA XFMR | 60400218 |  | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-02-06 | Goldmine | Moonridge Substation | Moonridge x Sheephorn | Big Bear Lake | 2051 | 251 | 514801 | 21.0777 | 42.8432 | Yes | Contact - Vegetation Weather | Yes | AR/Switch Actuated | Tree came down on wire, snow storm | 60400218 |  | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-02-06 | Goldmine | Moonridge Substation | Moonridge x Sheephorn | Big Bear Lake | 350 | 305 | 106750 | 4.3707 |  | Yes | Equipment Failure - Conuctor Failure |  |  | Same outage as above | 60400218 |  | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-02-06 | Garstin | Meadow Substation | St. Anton | Big Bear Lake | 27 | 133 | 3591 | 0.14703 |  | Yes | Equipment Failure - Conuctor Failure | Yes | TripSaver Actuated | Primary Down due to snow storm | 60400218 |  | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-02-06 | North Shore | Fawnskin Substation | Ridge Rd | Fawnskin | 20 | 478 | 9560 | 0.39142 |  | Yes | Contact - Vegetation Weather | Yes | No | Tree down on Primary due to snow storm | 60400218 |  | Green | No | No | 2 | No | Possible spark producing event; however wildfire risk low due to high moisture and low fuel in area. Tripsaver may have tripped before spark production.
S | Unplanned |  | 2024-02-06 | Sunset | Maple Substation | Sugarloaf | Sugarloaf | 1905 | 122 | 232410 | 9.5156 |  | Yes | Equipment Failure - Conuctor Failure | Yes | AR/Switch Actuated | Primary Down due to snow storm | 60400218 |  | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-02-06 | North Shore | Fawnskin Substation | North Shore Dr west of west boat ramp | Fawnskin | 250 | 192 | 48000 | 1.9653 |  | Yes | Equipment Failure - Conuctor Failure | Yes | TripSaver Actuated | Snow storm, wire down | 60400218 |  | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-02-06 | Radford | SCE Zanja Subsation | Converse Flats | Big Bear Lake | 3455 | 38 | 131290 | 5.3755 |  | Yes | Loss of Supply - SCE | No | AR/Switch Actuated | SCE Vista, Sanderson reports 33kV Bear Valley Line relayed and did not test | 60400218 |  | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-02-07 | Boulder | Village Substation | 39372 Big Bear Bl | Big Bear Lake | 1500 | 307 | 460500 | 18.8544 | 18.9066 | No | Contact - Vegetation Weather | No | AR/Switch Actuated | tree fell thru power lines tree opened AR105 |  |  | Green | No | No | 2 | No | Possible spark producing event; however wildfire risk low due to high moisture and low fuel in area. Tripsaver may have tripped before spark production.
S | Unplanned |  | 2024-02-07 | Sunset | Maple Substation | 466 Highland | Sugarloaf | 20 | 30 | 600 | 0.024566 |  | No | Contact - Vegetation Weather | No | No | open neutral in span due to tree branch falling during storm |  |  | Green | No | No | 2 | No | Possible spark producing event; however wildfire risk low due to high moisture and low fuel in area. Tripsaver may have tripped before spark production.
S | Unplanned |  | 2024-02-07 | Sunrise | Maple Substation | 526 Highland | Sugarloaf | 15 | 45 | 675 | 0.027637 |  | No | Contact - Vegetation Weather |  |  | Same outage as above |  |  | Green | No | No | 2 | No
S | Unplanned |  | 2024-03-09 | SCE Goldhill Ute Lines | SCE Goldhill Substation | SCE Lugo Sub. | Service Area Wide | 24753 | 61 | 1509933 | 61.8217 | 149.2789 | Yes | Loss of Supply - SCE | No | No | SCE Lugo reports a 115kV wire down plus setting issue at Goldhill |  |  | Green | No | No | 2 | No | No spark producing evnent
M | Unplanned |  | 2024-03-09 | SCE Goldhill Ute Lines | SCE Goldhill Substation | SCE Lugo Sub. | Service Area Wide | 20281 | 1 | 20281 | 0.83037 |  | Yes | Loss of Supply - SCE |  |  | Same outage as above |  |  | Green | No | No | 2 | No | No spark producing evnent
M | Unplanned |  | 2024-03-09 | SCE Goldhill Ute Lines | SCE Goldhill Substation | SCE Lugo Sub. | Service Area Wide | 7994 | 1 | 7994 | 0.3273 |  | Yes | Loss of Supply - SCE |  |  | Same outage as above |  |  | Green | No | No | 2 | No | No spark producing evnent
M | Unplanned |  | 2024-03-09 | SCE Goldhill Ute Lines | SCE Goldhill Substation | SCE Lugo Sub. | Service Area Wide | 3775 | 1 | 3775 | 0.15456 |  | Yes | Loss of Supply - SCE |  |  | Same outage as above |  |  | Green | No | No | 2 | No | No spark producing evnent
M | Unplanned |  | 2024-03-09 | SCE Goldhill Ute Lines | SCE Goldhill Substation | SCE Lugo Sub. | Service Area Wide | 24753 | 4 | 99012 | 4.0539 |  | Yes | Loss of Supply - SCE |  |  | Same outage as above |  |  | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-03-09 | SCE Goldhill Ute Lines | SCE Goldhill Substation | SCE Lugo Sub. | Service Area Wide | 24753 | 81 | 2004993 | 82.0911 |  | Yes | Loss of Supply - SCE |  |  | Same outage as above |  |  | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-03-14 | Country Club | Division Substation | 633 W. Aeroplane | Big Bear City | 20 | 480 | 9600 | 0.39306 | 0.39306 | No | Contact - Vegetation Weather | No | No | Tree fell on lines |  |  | Green | No | Yes | 2 | No | Possible spark producing event; however wildfire risk low due to high moisture and low fuel in area. Tripsaver may have tripped before spark production.
S | Unplanned |  | 2024-03-16 | Boulder | Village Substation | 40191 Big Bear Bl x Talmadge | Big Bear Lake | 2046 | 200 | 409200 | 16.754 | 33.2787 | No | Third Party - Car Hit Pole/Guy | No | No | Car Hit Pole |  |  | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-03-16 | Boulder | Village Substation | 40191 Big Bear Bl x Talmadge | Big Bear Lake | 2000 | 98 | 196000 | 8.0249 |  | No | Third Party - Car Hit Pole/Guy |  |  | Same outage as above |  |  | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-03-16 | Boulder | Village Substation | 40191 Big Bear Bl x Talmadge | Big Bear Lake | 200 | 1038 | 207600 | 8.4998 |  | No | Third Party - Car Hit Pole/Guy |  |  | Same outage as above |  |  | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-03-25 | North Shore | Fawnskin Substation | Fawnskin | Fawnskin | 500 | 14 | 7000 | 0.2866 | 0.53349 | No | Contact - Wire to wire slap | No | No | Outsource slapped wires together-AR805 tripped-composite cross arm broken |  |  | Green | No | No | 2 | No | Possible spark producing event; however wildfire risk low due to high moisture and low fuel in area. Tripsaver may have tripped before spark production.
S | Unplanned |  | 2024-03-25 | North Shore | Fawnskin Substation | Fawnskin | Fawnskin | 90 | 67 | 6030 | 0.24689 |  | No | Contact - Wire to wire slap |  |  | Same outage as above |  |  | Green | No | No | 2 | No | Possible spark producing event; however wildfire risk low due to high moisture and low fuel in area. Tripsaver may have tripped before spark production.
S | Unplanned |  | 2024-03-28 | Holcomb | Bear City Substation | Holcomb Circuit | Big Bear City | 1592 | 6 | 9552 | 0.39109 | 0.39109 | No | Contact - Wire to wire slap | No | AR/Switch Actuated | Outsource had a phase slipped out of a grip and contacted the secondary relaying the circuit slapped wires together-AR805 tripped-composite cross arm broken |  |  | Green | No | No | 2 | No | Possible spark producing event; however wildfire risk low due to high moisture and low fuel in area. Tripsaver may have tripped before spark production.
S | Unplanned |  | 2024-03-31 | North Shore | Fawnskin Substation | 1220 Ridge Rd. | Fawnskin | 25 | 60 | 1500 | 0.061415 | 0.061415 | No | Contact - Vegetation Weather | Yes | AR/Switch Actuated | Primary Neutral wire down. Opened TripSaver to make repairs |  |  | Green | No | No | 2 | No | Possible spark producing event; however wildfire risk low due to high moisture and low fuel in area. Tripsaver may have tripped before spark production.
S | Unplanned |  | 2004-04-29 | North Shore | Fawnskin Substation | 4kV NorthShore, Fawnskin Sub. | Fawnskin | 1521 | 48 | 73008 | 2.9892 | 2.9892 | No | Unknown | No | AR/Switch Actuated | Location unknown, patrolled 4kV Northshore and could not find a cause. Outsource was replacing a pole near North Shore Dr. x Bear Loop. They deny causing the outage. 4C Panel showed phase to ground fault: Ø=3,700 amps & ground 3,600 amps |  |  | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-06-03 | Goldmine | Moonridge Substation | 43350 Shasta Rd. | Big Bear City | 14 | 163 | 2282 | 0.093433 | 0.093433 | No | Equipment Failure - Fuse Holder | No | No | a porcelin cut-out broke on pole BV11386. The 18 amp fuse was still good, it just fell open due to the broken cut-out |  |  | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-06-09 | Goldmine | Moonridge Substation | 1142 Siskiyou | Big Bear Lake | 200 | 103 | 20600 | 0.84343 | 0.84343 | No | Other | No | TripSaver Actuated | House fire caused TripSaver to open |  |  | Yellow | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-06-18 | Boulder | Village Substation | Vilage Substation | Big Bear Lake | 2025 | 4 | 8100 | 0.33164 | 0.33164 | No | Operator Error | No | AR/Switch Actuated | Loading Engineering settings in 4kV Boulder CB100 Form 6 panel, CB tripped (settings mis-match) by Engineering | 604 00186 |  | Yellow | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-06-25 | Garstin | Meadow Substation | Meadow Substation | Big Bear Lake | 1069 | 1 | 1069 | 0.043768 | 0.043768 | No | Equipment Failure - AR/Switch | No | AR/Switch Actuated | Cold Load pck up - 4kV Garstin CB600 tripped | 604 00192 |  | Yellow | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-07-08 | Garstin | Meadow Substation | Summit x Switzerland | Big Bear Lake | 1069 | 43 | 45967 | 1.882 | 1.9901 | No | Contact - Wire to wire slap | No | AR/Switch Actuated | Object on wire caused phase to slap |  |  | Brown | No | No | 2 | No | Possible spark producing event; However, there is a lack of fuels in the area and the Tripsaver may have tripped before spark production.
S | Unplanned |  | 2024-07-08 | Garstin | Meadow Substation | Summit x Switzerland | Big Bear Lake | 60 | 44 | 2640 | 0.10809 |  | No | Contact - Wire to wire slap |  |  | Same outage as above |  |  | Brown | No | No | 2 | No
S | Unplanned |  | 2024-08-13 | Interlaken | Meadow Substation | 312 Crater Lake | Big Bear Lake | 2 | 80 | 160 | 0.0065509 | 0.0065509 | No | Equipment Failure - Fuse Holder | No | No | porcelain 100 amp cut-out broke in half |  |  | Yellow | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 8/26/202 | Interlaken | Division Substation | West of 4kV AR632 | Big Bear Lake | 275 | 24 | 6600 | 0.27023 | 0.27023 | No | Equipment Failure - Other | No | AR/Switch Actuated | When closing fuses on a 750kVA XFMR AR632 opened. Reverse feed thru the AR due to circuit configuration. Castle Glen circuit servicing load (normally Interlaken circuit). |  |  | Yellow | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-10-01 | Sunset | Maple Substation | 546 Inyo | Sugarloaf | 20 | 32 | 640 | 0.026204 | 0.026204 | No | Equipment Failure - Other | No | TripSaver Actuated | Broken hendrix insulator, conductor was floating, climbed pole to make repairs, de-energized due to location is heavily wood |  |  | Yellow | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-10-16 | Interlaken | Meadow Substation | 129 Olympic Dr / in World Mark | Big Bear Lake | 1 | 33 | 33 | 0.0013511 | 0.0013511 | No | Contact - Vehicle | No | TripSaver Actuated | BV Paving crew member ran into D.G. with equipment causing TS626 to open, TS625 on same pole remained closed |  |  | Yellow | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-10-31 |  | Moonridge Substation | 34kV Switzerland PS3469IR | Big Bear Lake | 3801 | 21 | 79821 | 3.2681 | 3.2681 | No | Equipment Failure - Other | No | AR/Switch Actuated | 34kV Switzerland PS3469IR pole #2 (middle) blew up. 44,832 AMPS at trip. Moonridge's 4kV Clubview & Goldmine plus Bear Mountain's 4kV Geronimo circuits off | 604 00151 |  | Yellow | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-11-14 | Lagunita | Village Substation | Lakeview x Mallard | Big Bear Lake | 800 | 43 | 34400 | 1.4085 | 1.4085 | No | Contact - Balloon | No | AR/Switch Actuated | Mylar Ballon went into primary and locked out circuit (AR145) |  |  | Yellow | No | No | 2 | No | Possible spark producing event; however wildfire risk low due to high moisture and low fuel in area. Tripsaver may have tripped before spark production.
S | Unplanned |  | 2024-12-05 | Boulder | Village Substation | 39756 Big Bear Bl | Big Bear Lake | 2 | 269 | 538 | 0.022028 | 0.022028 | No | Third Party - Car Hit Pole/Guy | No | No | Car hit pole, needed to replace pole from damage. | 60400264 |  | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-12-06 | Pioneer | Palomino Substation | 1837 Baldwin Lake Rd (across from) | Big Bear City | 7 | 48 | 336 | 0.013757 | 0.013757 | No | Equipment Failure - Transformer | No | No | broken secondary bushing on a 10KVA XFMR. | 60400218 |  | Green | No | No | 2 | No | No spark producing evnent
S | Unplanned |  | 2024-12-14 | Boulder | Village Substation | Waterview x Blue Jay | Big Bear City | 50 | 120 | 6000 | 0.24566 | 0.24566 | No | Equipment Failure - TripSaver | No | TripSaver Actuated | TripSaver opened after Radford switchover |  |  | Green | No | No | 2 | No | No spark producing evnent