## Table 12- WSD DR
Utility | Bear Valley Electric Service, Inc. | Notes:
Table No. | 12 | Risk-Spend-Efficiency (RSE) is defined as "An estimate of the cost-effectiveness of initiative, calculated by dividing the mitigation risk reduction benefit by the mitigation cost estimate based on the full set of risk reduction benefits estimated from the incurred costs."
Date Modified | 2021-03-05 | CAPEX = Capital expenditure; OPEX = Operating expenditure. In future submissions update planned spend, line miles treated, RSE, etc. with updated projections and actuals. Additional instructions can be found in QR information.
[23 empty] | Actual | Actual | Actual | Actual | Projected | Projected | Projected | Projected | Projected | Projected | Projected | Projected
Table 12: Mitigation initiative financials |  |  |  | Does BVES have a program that addresses this initative? |  | Does BVES anticipate devleoping a program that addresses this initiative? |  | Spend Aggregation | [14 empty] | CAPEX ($ thousands) | OPEX ($ thousands) | Line miles to be treated | Alternative units (if used) | CAPEX ($ thousands) | OPEX ($ thousands) | Line miles to be treated | Alternative units (if used) | CAPEX ($ thousands) | OPEX ($ thousands) | Line miles to be treated | Alternative units (if used)
Metric type | WMP Table # / Category | WMP Initiative # | Initative activity | Yes/No | If yes, where in the WMP is this addressed? (initative ID (e.g., A, B, etc.) and p. #) | Yes/ Exploring Possibility/ No | If so, when? (Quarter and Year) | List all intitative IDs included in spend aggregation (orange cells) | Primary driver targeted | Secondary driver targeted | Year initiated | Estimated RSE in non-HFTD region | Estimated RSE in HFTD Zone 1 | Estimated RSE in HFTD Tier 2 | Estimated RSE in HFTD Tier 3 | If existing: most recent proceeding that has reviewed program | If new: memorandum account | Current compiance status - In / exceeding compliance with regulations | Associated rule(s) - if multiple, separate by semi-colon - ";" | If spend not disaggregated by category, note spend category or mark general operations | Alternative units in which initiative is reported (if not line miles); still required to report line miles | Comments | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Total
Other | Risk Assessment & Mapping | 7.3.1.1 | A summarized risk map that shows the overall ignition probability and estimated wildfire consequence along the electric lines and equipment | Yes | Section 5.3 Table 5.3-1; Sec. 7.3.2.1 | Yes | Q2 2021 |  | Contact with vegetation | Other contact with object | 2018 | NA | NA | 3.28 | 3.28 | NA | WMP Memorandum Account | Exceeding Compliance | GO 95 |  |  | Bear Valley Electric Service has implemented the CPUC Fire Threat Map Adopted in D.17-12-024 December 14, 2017 throughout its service territory. This map shows the CPUC-designated fire hazard zone tiers within BVES's service territory, which quantify specific geography that could be subject to elevated fire risk under historically viable fire weather conditions. BVES has also identified seven sections of "at-risk" areas within its service territory based on the type of distribution facilities (overhead bare conductors, high voltage, etc.), tree and vegetation density, available dry fuel, and other factors that make certain locations more vulnerable to wildfire risk. The “at-risk” line sections are shown and further outlined in BVES's WMP submission. BVES's wildfire mapping efforts are foundational to determing and executing on priorities amongst BVES's risk mitigation efforts as well as its day-to-day operations. BVES employs tier designations to inform inspection, vegetation management, correction timeframes, and prioritized hardening efforts. Wildfire risk mapping is foundational to prioritizing efforts for a variety of activities undertaken throughout the business. Bear Valley Electric Service does not have a summarized risk map showing the overall ignition probability and estimated wildfire consequence, or match drop simulations, along electric lines and equipment. Within a future filing, BVES will develop a summarized risk map showing the overall ignition probability and estimated wildfire consequence along electric lines and equipment. This is planned starting in 2021 There are no specifically designated expenses, risk reductions, or any of the other column headings above associated with this initiative at this time. BVES is preparing the scope of work to implement these activities at the time of the Q4 EC QDR submission. In a future QDR filing , BVES will present its cost estimate to develop the models. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Other | Risk Assessment & Mapping | 7.3.1.2 | Climate-driven risk map and modelling based on various relevant weather scenarios | Yes | Section 5.3 Table 5.3-1; Sec. 7.3.2.1 | Yes | Q2 2021 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service has implemented the CPUC Fire Threat Map Adopted in D.17-12-024 December 14, 2017 throughout its service territory. This map shows the CPUC-designated fire hazard zone tiers within BVES's service territory, which quantify specific geography that could be subject to elevated fire risk under historically viable fire weather conditions. BVES has also identified seven sections of "at-risk" areas within its service territory based on the type of distribution facilities (overhead bare conductors, high voltage, etc.), tree and vegetation density, available dry fuel, and other factors that make certain locations more vulnerable to wildfire risk. The “at-risk” line sections are shown and further outlined in BVES's WMP submission. BVES's wildfire mapping efforts are foundational to determing and executing on priorities amongst BVES's risk mitigation efforts as well as its day-to-day operations. BVES employs tier designations to inform inspection, vegetation management, correction timeframes, and prioritized hardening efforts. Wildfire risk mapping is foundational to prioritizing efforts for a variety of activities undertaken throughout the business. Bear Valley Electric Service does not have a summarized risk map showing the overall ignition probability and estimated wildfire consequence, or match drop simulations, along electric lines and equipment. Within a future filing, BVES will develop a summarized risk map showing the overall ignition probability and estimated wildfire consequence along electric lines and equipment. This is planned starting in 2021 There are no specifically designated expenses, risk reductions, or any of the other column headings above associated with this initiative at this time. BVES is preparing the scope of work to implement these activities at the time of the Q4 EC QDR submission. In a future QDR filing , BVES will present its cost estimate to develop the models. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Other | Risk Assessment & Mapping | 7.3.1.3 | Ignition probability mapping showing the probability of ignition along the electric lines and equipment | Yes | Section 5.3 Table 5.3-1; Sec. 7.3.2.1 | Yes | Q2 2021 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service has implemented the CPUC Fire Threat Map Adopted in D.17-12-024 December 14, 2017 throughout its service territory. This map shows the CPUC-designated fire hazard zone tiers within BVES's service territory, which quantify specific geography that could be subject to elevated fire risk under historically viable fire weather conditions. BVES has also identified seven sections of "at-risk" areas within its service territory based on the type of distribution facilities (overhead bare conductors, high voltage, etc.), tree and vegetation density, available dry fuel, and other factors that make certain locations more vulnerable to wildfire risk. The “at-risk” line sections are shown and further outlined in BVES's WMP submission. BVES's wildfire mapping efforts are foundational to determing and executing on priorities amongst BVES's risk mitigation efforts as well as its day-to-day operations. BVES employs tier designations to inform inspection, vegetation management, correction timeframes, and prioritized hardening efforts. Wildfire risk mapping is foundational to prioritizing efforts for a variety of activities undertaken throughout the business. Bear Valley Electric Service does not have a summarized risk map showing the overall ignition probability and estimated wildfire consequence, or match drop simulations, along electric lines and equipment. Within a future filing, BVES will develop a summarized risk map showing the overall ignition probability and estimated wildfire consequence along electric lines and equipment. This is planned starting in 2021 There are no specifically designated expenses, risk reductions, or any of the other column headings above associated with this initiative at this time. BVES is preparing the scope of work to implement these activities at the time of the Q4 EC QDR submission. In a future QDR filing , BVES will present its cost estimate to develop the models. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Other | Risk Assessment & Mapping | 7.3.1.4 | Initiative mapping and estimation of wildfire and PSPS risk-reduction impact | Yes | Section 5.3 Table 5.3-1; Sec. 7.3.2.1 | Yes | Q2 2021 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service has implemented the CPUC Fire Threat Map Adopted in D.17-12-024 December 14, 2017 throughout its service territory. This map shows the CPUC-designated fire hazard zone tiers within BVES's service territory, which quantify specific geography that could be subject to elevated fire risk under historically viable fire weather conditions. BVES has also identified seven sections of "at-risk" areas within its service territory based on the type of distribution facilities (overhead bare conductors, high voltage, etc.), tree and vegetation density, available dry fuel, and other factors that make certain locations more vulnerable to wildfire risk. The “at-risk” line sections are shown and further outlined in BVES's WMP submission. BVES's wildfire mapping efforts are foundational to determing and executing on priorities amongst BVES's risk mitigation efforts as well as its day-to-day operations. BVES employs tier designations to inform inspection, vegetation management, correction timeframes, and prioritized hardening efforts. Wildfire risk mapping is foundational to prioritizing efforts for a variety of activities undertaken throughout the business. Bear Valley Electric Service does not have a summarized risk map showing the overall ignition probability and estimated wildfire consequence, or match drop simulations, along electric lines and equipment. Within a future filing, BVES will develop a summarized risk map showing the overall ignition probability and estimated wildfire consequence along electric lines and equipment. This is planned starting in 2021 There are no specifically designated expenses, risk reductions, or any of the other column headings above associated with this initiative at this time. BVES is preparing the scope of work to implement these activities at the time of the Q4 EC QDR submission. In a future QDR filing , BVES will present its cost estimate to develop the models. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Other | Risk Assessment & Mapping | 7.3.1.5 | Match drop simulations showing the potential wildfire consequence of ignitions that occur along the electric lines and equipment | Yes | Section 5.3 Table 5.3-1; Sec. 7.3.2.1 | Yes | Q2 2021 |  | PSPS - for sectionalization, etc. | Contact with vegetation | NA | NA | NA | 14.52 | 14.52 | GRC | WMP Memorandum Account | Exceeding Compliance | ESRB-8 | NA | NA | Bear Valley Electric Service has implemented the CPUC Fire Threat Map Adopted in D.17-12-024 December 14, 2017 throughout its service territory. This map shows the CPUC-designated fire hazard zone tiers within BVES's service territory, which quantify specific geography that could be subject to elevated fire risk under historically viable fire weather conditions. BVES has also identified seven sections of "at-risk" areas within its service territory based on the type of distribution facilities (overhead bare conductors, high voltage, etc.), tree and vegetation density, available dry fuel, and other factors that make certain locations more vulnerable to wildfire risk. The “at-risk” line sections are shown and further outlined in BVES's WMP submission. BVES's wildfire mapping efforts are foundational to determing and executing on priorities amongst BVES's risk mitigation efforts as well as its day-to-day operations. BVES employs tier designations to inform inspection, vegetation management, correction timeframes, and prioritized hardening efforts. Wildfire risk mapping is foundational to prioritizing efforts for a variety of activities undertaken throughout the business. Bear Valley Electric Service does not have a summarized risk map showing the overall ignition probability and estimated wildfire consequence, or match drop simulations, along electric lines and equipment. Within a future filing, BVES will develop a summarized risk map showing the overall ignition probability and estimated wildfire consequence along electric lines and equipment. This is planned starting in 2021 There are no specifically designated expenses, risk reductions, or any of the other column headings above associated with this initiative at this time. BVES is preparing the scope of work to implement these activities at the time of the Q4 EC QDR submission. In a future QDR filing , BVES will present its cost estimate to develop the models. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Other | Situational Awareness & Forecasting | 7.3.2.1 | Advanced weather monitoring and weather stations | Yes | Section 5.3 Tables 5.3-1, 5.3-2; Section 7.3.2.2(1) D (also C, E) |  |  | 7.3.2.1 | Fire weather conditions | Operational Practice Restrictions | 2018 | NA | NA | 8.4 | 8.4 | GRC | WMP Memorandum Account and GRC | In Compliance | GO 95 | NA | NA | Project Overview: Install additional 10 weather stations throughout the BVES service area, bringing the total to 20 weather stations. Allows BVES to prepare response ahead of time and take precautionary and/or advanced action. Also, allows BVES to validate actual conditions in the field such as before and after PSPS events. N/As: Bear Valley Electric Service has not calculated RSE values that differentiate between HFTD Tier 2 and Tier 3. Over the next period covering the WMP comprehensive update, BVES will make adjustments to its risk models to produce precise values. BVES' service territory is mostly HFTD Tier 2 with some HFTD Tier 3. "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 32241 | 0 | NA | 0 | 20000 | NA | 0 | 0 | NA | 0 | 0 | NA | 52241
Other | Situational Awareness & Forecasting | 7.3.2.2 | Continuous monitoring sensors | Yes | Section 7.3.2.2; Tables 5.3-1, 5.3-2 |  |  | 7.3.2.2 | Contact with vegetation | Other contact with object | 2020 | NA | NA | 3.98 | 3.98 | NA | WMP Memorandum Account | Exceeding Compliance | GO 95 | NA | NA | Project Overview: Install ALERT Wildfire HD Cameras throughout the service area allowing rapid detection and direction of first responders to any fires. N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 0 | 0 | NA | NA | 50000 | NA | 0 | 0 | NA | 0 | 0 | NA | 50000
Other | Situational Awareness & Forecasting | 7.3.2.3 | Fault indicators for detecting faults on electric lines and equipment | Yes | Section 5.3 Tables 5.3-1; Section 7.3.2.6(1) B |  |  | 7.3.2.3 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | BVES is monitoring Down wire Detection Technology and once the technology is ready for field use, BVES will develop a Down Wire Detection Installment Program in future WMPs. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | NA | NA | NA | NA | NA | NA | NA | NA | 149563 | NA | NA | NA | 149563
Other | Situational Awareness & Forecasting | 7.3.2.4 | Forecast of a fire risk index, fire potential index, or similar | Yes | Section 4.2 (also Table 4.2-3); Section 7.3.2.2(1) and Section 7.3.2.6(1) |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service has not established a plan to develop a forecast of a fire risk index, fire potential index, or similar beyond that which it has communicated in its 2019 and 2020 WMPs at this time. This will be considered for the scope of work addressing risk modeling tools starting mid-2021 to 2022. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. BVES's Subject Matter Expert evaluates the frequency of potential ignition events versus a set of impact categories (reliability, compliance, quality of service, safety and environmental) to develop total risk impact and scores. In addition, no specific incremental spend has been identified for this initiative. Bear Valley Electric Service does not have a proprietary model or methodology for evaluating the potential impact of ignitions. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Other | Situational Awareness & Forecasting | 7.3.2.5 | Personnel monitoring areas of electric lines and equipment in elevated fire risk conditions | Yes | Section 5.3 Table 5.3-1 |  |  | 7.3.2.5 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service does not have a specific wildfire mitigation situational awareness and forecasting initiative focused on personnel monitoring areas of electric lines and equipment in elevated fire risk conditions. During high fire threat weather that could lead to PSPS events, BVES does deploy crews to monitor conditions in the field, in the high threat areas. N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | NA | 9976 | NA | NA | NA | 42840 | NA | NA | NA | 43697 | NA | NA | 96513
Other | Situational Awareness & Forecasting | 7.3.2.6 | Weather forecasting and estimating impacts on electric lines and equipment | Yes | Section 4.2 (also Table 4.2-3); Section 7.3.2.2(1) and Section 7.3.2.6(1) |  |  | 7.3.2.6 | Contact with vegetation | Wire-to-wire contact | 2018 | NA | NA | 0.26 | 0.26 | NA | WMP Memorandum Account | Exceeding Compliance | ESRB-8 | NA | NA | Project. Installs complete Distribution Management Control Center with the following equipment and applications that provide full information capabilities available to Distribution decision makers relevant to the following functional areas: (1) Energy Resources (2) T&D Assets (3) SCADA, Outage Management System & GIS Other Applications (4) Weather Information (5) HD Cameras (6) Media access (Internet, BVES Website & Social Media, Local Radio, TV, etc. (7) Communications Equipment and (8) Dispatch services. N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 0 | 24000 | NA | NA | 0 | 45000 | NA | NA | NA | 45000 | NA | NA | 114000
Grid hardening | Grid Design & System Hardening | 7.3.3.1 | Capacitor maintenance and replacement program | Yes | Mentioned in Sec. 5.3 - covered as part of ongoing maintenance of subtrans/dist facilities |  |  |  | Equipment failure | Contamination | NA | NA | NA | NA | NA | NA | NA | NA | NA | Capacitor maintenance and replacement program | NA | Bear Valley Electric Service does not have a specific wildfire mitigation grid design and system hardening initiative focused on capacitor maintenance and replacement at this time. Bear Valley Electric Service has 25 capacitor locations and maintenance and replacement is included in the company's standard inspection, maintenance, and replacement protocols. The capacitors are fixed (either on service or off service) and part of our Overhead Facility Patrol and Inspection program objectives is to ensure they are not leaking or visually damaged. N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Grid hardening | Grid Design & System Hardening | 7.3.3.2 | Circuit breaker maintenance and installation to de-energize lines upon detecting a fault | Yes | Mentioned in Sec. 5.3 - covered as part of ongoing maintenance of subtrans/dist facilities |  |  |  | Equipment failure | PSPS - for sectionalization, etc. | NA | NA | NA | NA | NA | NA | NA | NA | NA | Circuit breaker maintenance and installation to de-energize lines upon detecting a fault | NA | Bear Valley Electric Service does not have a specific wildfire mitigation grid design and system hardening initiative focused on circuit breaker maintenance and replacement at this time. Circuit breakers are generally installed for all distribution circuits to detect fault current and protect equipment in the event that a fault is detected. Circuit breaker replacement and maintenance is included in the company’s standard inspection, maintenance, and replacement protocols. Any enhanced inspections or accelerated correction timeframe/replacements are captured in Asset management and inspections under Section 7.3 of the WMP. Installation of system automation equipment. N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Grid hardening | Grid Design & System Hardening | 7.3.3.3 | Covered conductor installation | Yes | Section 5.3 Tables 5.3-1 & 5.3-2; Section 7.1 table 7.1-1; Section 7.3.2.3(1)I-L |  |  | 7.3.3.3 | Contact with vegetation | Wire-to-wire contact | 2019 | NA | NA | 0.02 | 0.02 | NA | WMP Memorandum Account | NA | NA | NA | NA | 2019 and 2020 costs include the Covered Conductor Replacement Pilot Program and the Covered Conductor Wrap Pilot Program. Program replaces all 205.2 line miles of 34.5 kV overhead sub-transmission lines (beginning in 2020) and 4 kV distribution lines (beginning in 2021) with covered wire over a 6-year period, 2020-2026. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 3057088 | 0 | 22.5 | NA | 5438095 | 0 | 38.7 | NA | 5438095 | NA | 38.7 | NA | 13933278
Grid hardening | Grid Design & System Hardening | 7.3.3.4 | Covered conductor maintenance | Yes | Section 5.3 Tables 5.3-1 & 5.3-2; Section 7.1 table 7.1-1; Section 7.3.2.3(1)I-L |  |  |  | Contact with vegetation | Wire-to-wire contact | 2019 | NA | NA | NA | NA | NA | NA | NA | NA | Covered conductor maintenance |  | Bear Valley Electric Service does not have specific wildfire mitigation grid design and system hardening initiatives focused on covered conductor maintenance. As BVES progresses with its implementation of its wildfire mitigation initiatives, BVES will continue to evaluate covered conductor maintenance initiatives specific to wildfire mitigation. N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Grid hardening | Grid Design & System Hardening | 7.3.3.5 | Crossarm maintenance, repair, and replacement | Yes | Mentioned in Sec. 5.3 - covered as part of ongoing maintenance of subtrans/dist facilities |  |  |  | Equipment failure | Other contact with object | NA | NA | NA | NA | NA | NA | NA | NA | NA | Crossarm maintenance, repair, and replacement | NA | Bear Valley Electric Service does not have a specific wildfire mitigation grid design and system hardening initiative focused on crossarm maintenance, repair, and replacement at this time. Routine crossarm maintenance, repair, and replacement are included in the company’s standard inspection and correction programs, with an accelerated timeline for correction under the company’s Inspection program improvement N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Grid hardening | Grid Design & System Hardening | 7.3.3.6 | Distribution pole replacement and reinforcement, including with composite poles | Yes | Mentioned in Sec. 5.3 - covered as part of ongoing maintenance of subtrans/dist facilities; Sec 7.3.2.3(1)H |  |  | 7.3.3.6; 7.3.3.13; 7.3.4.13 | Equipment failure | Wire-to-wire contact | 2018 | NA | NA | 0.09 | 0.09 | D. 19-08-027 | NA | In Compliance | GO 95 | NA | NA | Test all poles to loading standards, GO95 requirements, intrusive inspection criteria and age and then, replaces or remediates non-compliant poles. N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 2546759.56 | 0 | NA | NA | 1553097 | 0 | NA | NA | 1553097 | 0 | NA | NA | 5652953.56
Grid hardening | Grid Design & System Hardening | 7.3.3.7 | Expulsion fuse replacement | Yes | Sec. 5.3 Tables 5.3-1 & 5.3-2 |  |  | 7.3.3.7 | Equipment failure | Other contact with object | 2018 | NA | NA | 0.09 | 0.09 | R. 18-10-007 | NA | Exceeding Compliance | GO 95 | NA | NA | Replaces all conventional (expulsion) fuses with current limiting (ELF) and electronic fuses (Fuse TripSavers). N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 3559483.68 | 0 | NA | NA | 741850 | 0 | NA | NA | 0 | 0 | NA | NA | 4301333.68
Grid hardening | Grid Design & System Hardening | 7.3.3.8 | Grid topology improvements to mitigate or reduce PSPS events | Yes | Section 5.3 Table 5.3-1 |  |  |  | Other contact with object | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | Grid topology improvements to mitigate or reduce PSPS events | NA | Bear Valley Electric Service does not have a specific wildfire mitigation grid design and system hardening initiative focused on grid topology improvements to mitigate or reduce PSPS events in addition to those described elsewhere in Table 12 N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Grid hardening | Grid Design & System Hardening | 7.3.3.9 | Installation of system automation equipment | Yes | Section 5.3 Tables 5.3-1 &5.3-2; Sec. 7.1 Table 7.1-1; Sec. 7.3.2.2(1)G (also A of that subsec), 7.3.2.2(3) Table 7.3.2.2-1, Sec 7.3.2.2(4) Table 7.3.3.2-2 |  |  | 7.3.3.9 | Equipment failure | Wire-to-wire contact | 2019 | NA | NA | 0.26 | 0.26 | D. 19-08-027 | NA | In Compliance | NA | NA | NA | Install grid automation. Fully instruments and automates BVES grid. Consists of installing a service area wide network operating on a SCADA system, substation automation, remote fault indicators, remote metering and power sensors and remote switching equipment to enable BVES to significantly improve its capability to detect and isolate faults rapidly before ever rolling out a crew. N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 1253247 | 0 | NA | NA | 1315933 | 0 | NA | NA | 915833 | 0 | NA | NA | 3485013
Grid hardening | Grid Design & System Hardening | 7.3.3.10 | Maintenance, repair, and replacement of connectors, including hotline clamps | Yes | Mentioned in Sec. 5.3 - covered as part of ongoing maintenance of subtrans/dist facilities |  |  |  | Equipment failure | Wire-to-wire contact | NA | NA | NA | NA | NA | NA | NA | NA | NA | Maintenance, repair, and replacement of connectors, including hotline clamps | NA | Bear Valley Electric Service does not have a specific wildfire mitigation grid design and system hardening initiative focused on maintenance, repair, and replacement of connectors, including hotline clamps at this time. Replacement of connectors, where applicable, is included in other programs such as installation of covered conductor. N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Grid hardening | Grid Design & System Hardening | 7.3.3.11 | Mitigation of impact on customers and other residents affected during PSPS event | Yes | Section 5.3 Table 5.3.1-1; Section 4.5.1 Section 7.3.2.10; Section 8.1, 8.2(1-2), 8.4(1, 4); See also Appendix A esp Appendix C to the PSPS Plan. BVES Sectionalized its system by circuits ads described in Sec. 4.2. Any PSPS would be initialized by section if such an activiation were required |  |  |  | PSPS - for sectionalization, etc. | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | Mitigation of impact on customers and other residents affected during PSPS event | NA | Bear Valley Electric Service does not have specific wildfire mitigation grid design and system hardening initiatives focused on mitigation of impact on customers and other residents affected during PSPS events Both of these programs are combined as relevant grid topology improvements pertaining to grid design and system hardening that reduce PSPS events inherently also mitigate the impact on customers. Furthermore, BVES’s additional programs or efforts to mitigate the impact on customers and other residents affected during a PSPS event are captured later in this Table (12) N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Grid hardening | Grid Design & System Hardening | 7.3.3.12 | Other corrective action | No | N/A | No | N/A | 7.3.3.12 | Other contact with object | Equipment failure | 2019 | NA | NA | 0.01 | 0.01 | NA | WMP Memorandum Account | Exceeding Compliance | GO 95 | NA | NA | Replaces the 34.5 kV Radford Line (2.82 overhead circuit miles/8.46 line miles) with covered power lines and poles that are resistant to fire. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 159928 | 0 | 0 | NA | 5443764 | 0 | 8.46 | NA | 0 | 0 | 0 | NA | 5603692
Grid hardening | Grid Design & System Hardening | 7.3.3.13 | Pole loading infrastructure hardening and replacement program based on pole loading assessment program | Yes | Section 5.3 Table 5.3-1 & Table 5.3-2; Sec. 7.3.2.3 esp. part(1)H |  |  |  | Equipment failure | Contamination | NA | NA | NA | NA | NA | NA | NA | NA | NA | Pole loading infrastructure hardening and replacement program based on pole loading assessment program | NA | Bear Valley Electric Service's pole loading infrastructure hardening and replacement program based on pole loading assessment program is encompassed by and addressed in WMP Initiative # 5.3.4.6. Intrusive pole inspections. Under this initiative, BVES tests all poles to loading standards, GO95 requirements, intrusive inspection criteria and age, and then replaces or remediates non-compliant poles. N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Grid hardening | Grid Design & System Hardening | 7.3.3.14 | Transformers maintenance and replacement | Yes | Mentioned in Sec. 5.3 - covered as part of ongoing maintenance of subtrans/dist facilities |  |  |  | Equipment failure | Contamination | NA | NA | NA | NA | NA | NA | NA | NA | NA | Transformers maintenance and replacement | NA | Bear Valley Electric Service does not have a specific wildfire mitigation grid design and system hardening initiative focused on transformer maintenance and replacement. Transformer replacement and maintenance is included in the company’s standard inspection, maintenance, and replacement protocols. N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Grid hardening | Grid Design & System Hardening | 7.3.3.15 | Transmission tower maintenance and replacement | No | N/A | No | N/A |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service does not have a specific wildfire mitigation grid design and system hardening initiative focused on transmission tower maintenance and replacement because BVES does not own any transmission. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Grid hardening | Grid Design & System Hardening | 7.3.3.16 | Undergrounding of electric lines and/or equipment | No | N/A | No | No current planning for any additional undergrounding |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | The SCE Ute Lines (1 & 2), which only serve BVES, consists of approximately 1.5 miles of overhead sub-transmission bare lines (34.5 kV) that connect the BVES system at two points with the SCE Goldhill Switch Station. The Ute Lines (1 & 2) run on the same poles for a large section of the circuit. These SCE assets are located in the U.S. Forest Service area and in an environmentally sensitive area known as the “pebble plane”. These lines provide approximately 72% of rated supply capacity and, under normal conditions, 100% of BVES’ supply loads. These lines allow BVES to adopt a defensive operational scheme during the fire season by allowing the de-energization of the Radford Line (from the Redlands), which mostly traverses a High Fire Threat District (“HFTD”) Tier 3 area. The Ute Lines (1 & 2) are completely in a HFTD Tier 2 area. Therefore, these lines are critical to BVES’ energy supply and reliability and permit BVES to significantly mitigate risk of wildfire in its HFTD Tier 3 area. BVES does not intend to pursue this project further, but intends to pursue other options with SCE to resolve the inherent wildfire risk exposure, and system safety and reliability risk of the Ute lines. Under this WMP, BVES does not propose to underground any overhead lines. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Grid hardening | Grid Design & System Hardening | 7.3.3.17 | Updates to grid topology to minimize risk of ignition in HFTDs | Yes | Section 5.3, Table 5.3-1: BVES’s entire service area is in the HFTD 2 & 3. Sectionalizing between HFTD 2 and 3 already in place. Further sectionalizing within the HFTD to isolate “higher risk areas” already in place. |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | Bear Valley Electric Service does not have any specific grid design and system hardening wildfire mitigation initiatives focused on updates to grid topology to minimize risk of ignition in HFTDs at this time. BVES recognizes that it should continue to evaluate updates to grid topology as weather patterns change and overall modeling and assessments evolve. Other grid design and system hardening programs include, as a component, grid topology improvements to minimize the risk of ignition in the HFTD. BVES recognizes that it is challenging to mitigate wildfire risk through grid topology changes alone and therefore focuses more on augmentation of existing circuitry through system hardening efforts . | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Asset inspection | Asset Management & Inspections | 7.3.4.1 | Detailed inspections of distribution electric lines and equipment | Yes | Section 5.3 Table 5.3-1; Section 7.3.2.4 esp part (1)C |  |  | 7.3.4.1 | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | Detailed inspections of distribution electric lines and equipment | NA | Bear Valley Electric Service has not specified a wildfire mitigation asset management and inspections initiative for detailed inspections of distribution lines and equipment. BVES's distribution inspection initiatives are best captured in 5.3.4.11. Patrol inspections of distribution lines and equipment | 0 | 72325 | 42 | NA | 0 | 120000 | 42 | NA | 0 | 120000 | 42 | NA | 312325
Asset inspection | Asset Management & Inspections | 7.3.4.2 | Detailed inspections of transmission electric lines and equipment | No | N/A | No | N/A |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service does not have any transmission lines or equipment as all of BVES's lines are below 65 kV. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Asset inspection | Asset Management & Inspections | 7.3.4.3 | Improvement of inspections | Yes | Section 5.3 Table 5.3-1; Section 7.3.2.4 esp Table 7.3.2.4-2 |  |  |  | Equipment failure | Wire-to-wire contact | 2019 | NA | NA | NA | NA | R. 18-10-007 | NA | In Compliance | GO 95; GO 165 | Improvement of inspections | NA | Improvements of Bear Valley Electric Service's inspections have already been captured in other initiatives | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Asset inspection | Asset Management & Inspections | 7.3.4.4 | Infrared inspections of distribution electric lines and equipment | Yes | Section 5.3 Table 5.3-1; Section 7.3.2.4 esp part (1)E |  |  |  | Other contact with object | Equipment failure | 2018 | NA | NA | 0.8 | 0.8 | GRC | NA | Exceeding Compliance | Go 95 | NA | NA | Contract Exacter Services. Conduct survey of BVES overhead system on 3-year cycle using infrared, ultrasonic and EMI sensors. Approximately 1/3 of OH system surveyed each year.” to read: “Contract Exacter Services. Conducted survey of BVES overhead system using infrared, ultrasonic and EMI sensors. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 0 | 0 | 0 | NA | 0 | 0 | 0 | NA | 0 | 0 | 0 | NA | 0
Asset inspection | Asset Management & Inspections | 7.3.4.5 | Infrared inspections of transmission electric lines and equipment | No | N/A | No | N/A |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service does not have any transmission lines or equipment as all of BVES's lines are below 65 kV. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Asset inspection | Asset Management & Inspections | 7.3.4.6 | Intrusive pole inspections | Yes | Section 5.3 Table 5.3-1; Section 7.3.2.4 esp part (1)F |  |  |  | Equipment failure | Contamination | NA | NA | NA | NA | NA | NA | NA | NA | NA | Intrusive pole inspections |  | Test all poles to loading standards, GO95 requirements, intrusive inspection criteria and age and then, replaces or remediates non-compliant poles. Covered under 5.3.3.6. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Asset inspection | Asset Management & Inspections | 7.3.4.7 | LiDAR inspections of distribution electric lines and equipment | Yes | Section 5.3 Tables 5.3-1, 5.3-2; Section 7.3.2.4 esp part (1)D |  |  | 7.3.4.7; 7.3.5.7 | Other contact with object | Equipment failure | 2018 | NA | NA | 0.7 | 0.7 | NA | WMP Memorandum Account | Exceeding Compliance | GO 95 | NA | NA | Conduct LiDAR surveys of BVES overhead system on a semi-annual basis. N/As: BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 0 | 210120 | 211 | NA | 0 | 240000 | 211 | NA | 0 | 240000 | 211 | NA | 690120
Asset inspection | Asset Management & Inspections | 7.3.4.8 | LiDAR inspections of transmission electric lines and equipment | No | N/A | No | N/A |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service does not have any transmission lines or equipment as all of BVES's lines are below 65 kV. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Asset inspection | Asset Management & Inspections | 7.3.4.9 | Other discretionary inspection of distribution electric lines and equipment, beyond inspections mandated by rules and regulations | Yes | Section 5.3 Table 5.3-1; Section 7.2(C); Section 7.3.2.4(1)B | Yes | UAV; released bid for proposals in early 2021 | 7.3.4.8 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service does not have any wildfire mitigation asset management and inspection initiatives focused on other discretionary inspections of distribution electric lines and equipment beyond inspections mandated by rules and regulations at this time that have not been captured in other initiatives. | 0 | 77070 | 211 | NA | 0 | 90000 | 211 | NA | 0 | 90000 | 211 | NA | 257070
Asset inspection | Asset Management & Inspections | 7.3.4.10 | Other discretionary inspection of transmission electric lines and | No | N/A | No | N/A |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service does not have any transmission lines or equipment as all of BVES's lines are below 65 kV. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Asset inspection | Asset Management & Inspections | 7.3.4.11 | Patrol inspections of distribution electric lines and equipment (combined with Detailed Inspection Costs) | Yes | Section 5.3 Table 5.3-1; Section 7.1(1&2), Section 7.3.2.4 esp part (1)A & B |  |  |  | Other contact with object | Equipment failure | 2018 | NA | NA | 0.09 | 0.09 | NA | WMP Memorandum Account | Exceeding Compliance | GO 95 | NA | NA | Conduct annual 2nd Ground Patrol of overhead facilities by 3rd party. This is in addition to BVES GO-165 annual ground patrol. N/As: BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 0 | NA | 211 | NA | 0 | NA | 211 | NA | 0 | NA | 211 | NA | 0
Asset inspection | Asset Management & Inspections | 7.3.4.12 | Patrol inspections of transmission electric lines and equipment | No | N/A | No | N/A |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service does not have any transmission lines or equipment as all of BVES's lines are below 65 kV. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Asset inspection | Asset Management & Inspections | 7.3.4.13 | Pole loading assessment program to determine safety factor | Yes | Section 5.3 Table 5.3-1 & Table 5.3-2; Sec. 7.3.2.3 esp. part(1)H |  |  |  | Equipment failure | Contamination | NA | NA | NA | NA | NA | NA | NA | NA | NA | Pole loading assessment program to determine safety factor | NA | Bear Valley Electric Service's wildfire mitigation asset management and inspections pole loading assessment program to determine safety factor is fully captured in 5.3.4.6.. Intrusive pole inspections. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Asset inspection | Asset Management & Inspections | 7.3.4.14 | Quality assurance / quality control of inspections | No | Section 5.3 Table 5.3-1 | Exploring Possibility | To be determined |  | Equipment failure | Other contact with object | NA | NA | NA | NA | NA | NA | NA | NA | NA | Quality assurance / quality control of inspections | NA | General initiative and best practices applied to and accounted for in other relevant initiatives | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Asset inspection | Asset Management & Inspections | 7.3.4.15 | Substation inspections | Yes | Section 5.3 Table 5.3-1; Sec. 7.3.2.4 esp. part(1)G - I |  |  | 7.3.4.14 | Equipment failure | Vandalism / Theft | NA | NA | NA | NA | NA | NA | NA | NA | NA | Substation inspections | NA | Bear Valley Electric Service's substation inspections are fully captured in 5.3.4.11. Patrol inspections of distribution electric lines and equipment | 0 | 160287 | NA | NA | 0 | 107678 | NA | NA | NA | 107678 | NA | NA | 375643
Vegetation management project | Vegetation Management & Inspections | 7.3.5.1 | Additional efforts to manage community and environmental impacts | No | BVES currently has not encountered the need for additional efforts to manage community and environmental impact | No | N/A |  | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service does not have a specific wildfire mitigation vegetation management and inspection initiative dedicated to this effort at this time. BVES recognizes that additional efforts to manage community and environmental impacts are critical to reducing wildfire risk and conducts such efforts on an as-needed basis, as well as incorporating additional efforts within other programs such as those in Stakeholer Cooperation and Community Engagement, and Emergency Planning. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.2 | Detailed inspections of vegetation around distribution electric lines and equipment | Yes | Performed at same time as asset inspections. See Section 5.3 Table 5.3-1; Section 7.3.2.4 esp part (1)C |  |  |  | Contact with vegetation | Equipment failure | 2019 | NA | NA | 0.35 | 0.35 | D.19-08-027 | NA | Exceeding Compliance | GO-95 | NA | NA | Increases vegetation clearances, criterial for tree removals, and eliminates overhang on sub-transmission. These are above the 2017 baseline vegetation clearances that were in effect before CPUC Decision 17-12-024 was adopted. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.3 | Detailed inspections of vegetation around transmission electric lines and equipment | No | N/A | No | N/A |  | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service does not have any transmission lines or equipment as all of BVES's lines are below 65 kV. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Vegetation management project | Vegetation Management & Inspections | 7.3.5.4 | Emergency response vegetation management due to red flag warning or other urgent conditions | Yes | Section 5.3, Table 5.3-1; Sec. 7.3.2.5(1)A |  |  |  | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service does not have a specific wildfire mitigation vegetation management and inspection initiative dedicated to this effort at this time. BVES recognizes that emergency response vegetation management due to red flag warnings or other urgent conditions are critical to reducing wildfire risk and has already incorporated these efforts into BVES's existing Emergency Response and Preparedness Plan as well as the initiatives described in Grid Operations and Protocols. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Vegetation management project | Vegetation Management & Inspections | 7.3.5.5 | Fuel management and reduction of “slash” from vegetation management activities | Yes | All slash taken daily - see Section 5.3, Table 5.3-1; Sec. 7.3.2.5 parts (1) A&C |  |  |  | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service does not have a specific wildfire mitigation vegetation management and inspection initiative dedicated to this effort at this time. Fuel management and reduction of "slash" from vegetation management activities have been incorporated into BVES's ongoing and newly proposed vegetation management initiatives as described in Vegetation Management. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.6 | Improvement of inspections | Yes | BVES conducts vegetation inspections in tandem with asset/equipment inspections utilizing the same schedules and methods - continual improvement; Section 5.3 Table 5.3-1; Section 7.3.2.4 esp Table 7.3.2.4-2 |  |  |  | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | Quality assurance / quality control of vegetation inspections | NA | Costs are assocated with initiative 5.3.5.11 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.7 | LiDAR inspections of vegetation around distribution electric lines and equipment | Yes | Same as with asset inspections - Section 5.3 Tables 5.3-1, 5.3-2; Section 7.3.2.4 esp part (1)D |  |  |  | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service's LiDAR inspections of vegetation around distribution electric lines and equipment are captured in LiDAR inspections of distribution electric lines and equipment. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.8 | LiDAR inspections of vegetation around transmission electric lines and equipment | No | N/A | No |  |  | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service does not have any transmission lines or equipment as all of BVES's lines are below 65 kV. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.9 | Other discretionary inspections of vegetation around distribution electric lines and equipment | Yes | Same as with asset inspections - Section 5.3 Table 5.3-1; Section 7.2(C); Section 7.3.2.4(1)B |  |  |  | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service does not have any other discretionary inspections of vegetation around distribution electric lines and equipment beyond inspections mandated by rules and regulations and other described initiatives at this time. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.10 | Other discretionary inspections of vegetation around transmission electric lines and equipment | No | N/A | No | N/A |  | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service does not have any transmission lines or equipment as all of BVES's lines are below 65 kV. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.11 | Patrol inspections of vegetation around distribution electric lines and equipment | Yes | Same as with asset inspections - Section 5.3 Table 5.3-1; Section 7.1(1&2), Section 7.3.2.4 esp part (1)A & B |  |  |  | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service's patrol inspections of vegetation around distribution electric lines and equipment are fully captured in Detailed inspection of vegetation around distribution electric lines and equipment and Patrol inspections of distribution electric lines and equipment. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.12 | Patrol inspections of vegetation around transmission electric lines and equipment | No | N/A | No | N/A |  | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service does not have any transmission lines or equipment as all of BVES's lines are below 65 kV. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.13 | Quality assurance / quality control of vegetation inspections | No | N/A | Exploring Possibility | To be determined |  | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | Quality assurance / quality control of vegetation inspections | NA | Costs are assocated with initiative 5.3.5.11 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Vegetation management project | Vegetation Management & Inspections | 7.3.5.14 | Recruiting and training of vegetation management personnel | Yes | Section 5.3 Table 5.3-1; Section 5.4 including Tables 5.4.2-1, 5.4.3-1 |  |  | 7.3.5.14 | Contact with vegetation | Equipment failure | 2020 | NA | NA | 0.58 | 0.58 | GRC | WMP Memorandum Account | Exceeding Compliance | GO-95 | NA | NA | Places a full-time contract utility forester as part of the BVES team. The job duties of the contract forester would include: Inspections: Inspect and evaluate circuits for hot spot locations, hazard tree identification and outage investigations. Auditing: Perform site-specific work audits to ensure contractors are performing within the specifications set forth by BVES. Customer Contacts/Issue Resolution: initiate or follow up in a timely and professional manner on all customer issues that may arise in a manner that will support the policies and procedures of BVES. This includes customer notifications, permit negotiations, conflict resolution, outage support/investigations and providing shared resources to construction, substation, lines and/or various work groups related to BVES’s Vegetation Management group. Administrative: Perform data entry, spreadsheet work, monitor crew activity sheets, track completed work, capture photo documentation of specific conditions and other administrative tasks as needed. Developing Work Plans: Develop work plans that specify the pruning and removal requirements to maintain BVES ROWs. These plans will be developed in an efficient and straightforward manner for a seamless transition to the tree contractors. Specialized Projects: Develop and manage specialized projects with an emphasis on reliability and risk management. Perform enhanced outage investigations, integrated storm hardening projects, performed risk assessment and prioritization studies, developed storm response protocols and implemented hazard tree programs that are focused on improving system safety. Contractor Safety Observations: Observe contractors as they work and provide safety behavior modification to help ensure a program that is best in class not only in vegetation management, but safety as well. RSE is an estimate based on latest available risk assessment. | NA | 0 | NA | NA | NA | 147900 | NA | NA | NA | 150858 | NA | NA | 298758
Vegetation management project | Vegetation Management & Inspections | 7.3.5.15 | Remediation of at-risk species | No | Section 5.3 Table 5.3.1 - Currently BVES has not had this issue. BVES has discussed this with its VM contractor should this be a future problem. Additionally, BVES will be bringing on a Forester in April 2021 to review this more closely |  |  |  | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Remediation of at-risk species is a subset to the company’s vegetation management practices to achieve clearances around electric lines and equipment as well as being outlined in the reoccuring training of vegetation managment personnel. As such, Bear Valley Electric Service does not have a specific wildfire mitigation initiative for remediation of at-risk species at this time. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Vegetation management project | Vegetation Management & Inspections | 7.3.5.16 | Removal and remediation of trees with strike potential to electric lines and equipment | Yes | Section 5.3, Table 5.3.1-1; Sec. 7.3.2.5(1)A |  |  |  | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Removal and remediation of trees with strike potential to electric lines and equipment is a subset to the company’s vegetation management practices to achieve clearances around electric lines and equipment as described in reoccuring training of vegetation management personnel. As such, Bear Valley Electric Service does not have a specific wildfire mitigation initiative for removal and remediation of trees with strike potential at this time. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.17 | Substation inspection | Yes | Same as with asset inspections - Section 5.3 Table 5.3-1; Sec. 7.3.2.4 esp. part(1)G - I |  |  |  | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Substation vegetation management is a subset to the company’s overall vegetation management initiatives as described in Vegetation Management | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Vegetation management project | Vegetation Management & Inspections | 7.3.5.18 | Substation vegetation management | Yes | Same as with asset inspections - Section 5.3 Table 5.3-1; Sec. 7.3.2.4 esp. part(1)G - I |  |  | 7.3.5.18 | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Substation inspections are a subset to the company’s overall vegetation management inspections as described in Detailed Inspection of vegetation around distribution e;ectric lines and equipemnt, and Recruitting and training of vegetation management personnel | NA | 9410 | NA | NA | NA | 12000 | NA | NA | NA | 12000 | NA | NA | 33410
Vegetation management project | Vegetation Management & Inspections | 7.3.5.19 | Vegetation inventory system | Yes | Section 5.3, Table 5.3.1-1 |  |  |  | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service does not have a specific wildfire mitigation initiative dedicated to the creation and management of a vegetation inventory system at this time. The company's utility forester, as described in Recruitting and training of vegetation management personnel, maintains such a system. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Vegetation management project | Vegetation Management & Inspections | 7.3.5.20 | Vegetation management to achieve clearances around electric lines and equipment | Yes | Section 5.4.2 Section 7.3.2.5 |  |  | 7.3.5.2; 7.3.5.5; 7.3.5.11; 7.3.5.13; 7.3.5.16; 7.3.5.17; 7.3.5.19; 7.3.5.20 | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Vegetation management to achieve clearances around electric lines and equipment is captured in Detailed Inspection of vegetation around distribution electric lines and equipemnt, and Recruitting and training of vegetation management personnel | 0 | 2070651 | NA | NA | 0 | 2600000 | NA | NA | 0 | 2600000 | NA | NA | 7270651
Other | Grid Operations & Operating Protocols | 7.3.6.1 | Automatic recloser operations | Yes | Supporting Table 7.3.2.6-1; Appendix |  |  | 7.3.6.1 | Other contact with object | Equipment failure | 2019 | NA | NA | 0.41 | 0.41 | D.19-08-027 | GRC | NA | NA | NA | NA | Automatic Recloser Upgrades. Recloser replacement to reduce electrical sparking, while also helping mitigate power outages and equipment damage. Estimated 33% completion in 2019. | 290458.75 | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 290458.75
Other | Grid Operations & Operating Protocols | 7.3.6.2 | Crew-accompanying ignition prevention and suppression resources and services | Yes | Under the Emergency Preparedness & Response Plan, Section 7.3.2.9, and in Appendix B. |  |  |  | Other contact with object | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service does not currently deploy crew-accompanying ignition prevention and suppression resources and services as part of its routine operational practices. When an emergency occurs, BVES communicates and collaborates with local emergency response teams, which can include crew-accompanying ignition prevention and suppression resources and services. Additionally, during elevated risk conditions or during fire season, BVES leverages specific work practices and protocols and makes available specific resources and tools for use by operations personnel as included in Grid Operation and Protocols. However, BVES does not currently have a specific grid operations and protocols wildfire mitigation initiative focused on crew-accompanying ignition prevention and suppression resources and services. The use of these services will be re-evaluated and considered for future incorporation as part of the annual WMP review process. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Other | Grid Operations & Operating Protocols | 7.3.6.3 | Personnel work procedures and training in conditions of elevated fire risk | Yes | BVES Fire Prevention Procedures - Appendix A, Section 4.3 |  |  | 7.3.6.3; 7.3.6.4; 7.3.6.5 | Other contact with object | Equipment failure | 2019 | NA | NA | 2.23 | 2.23 | D.19-08-027 | GRC | NA | NA | NA | NA | Wildfire Infrastructure Protection Teams. Roles and responsibilities for staff to respond to protect system infrastructure in case of emergencies. | NA | 0 | NA | NA | NA | 42840 | NA | NA | NA | 43696 | NA | NA | 86536
Other | Grid Operations & Operating Protocols | 7.3.6.4 | Protocols for PSPS re-energization | Yes | Section 8 and PSPS Plan |  |  |  | Other contact with object | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service considers re-energization after a PSPS event to be a subset of outage restoration and re-energization protocols generally included in Grid Operations and Protocol Therefore, the BVES does not have a separate protocol for PSPS. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Other | Grid Operations & Operating Protocols | 7.3.6.5 | PSPS events and mitigation of PSPS impacts | Yes | Section 8 and PSPS Plan, BVES Sectionalized its system by circuits ads described in Sec. 4.2. Any PSPS would be initialized by section if such an activiation were required. |  |  | 7.3.6.3; 7.3.6.4; 7.3.6.5 | Other contact with object | Other contact with object | 2019 | NA | NA | 5.26 | 5.26 | D.19-08-027 | GRC and Fire Hazard Prevt. Memorandum Account | In Compliance | R.18-12-005 | NA | NA | PSPS Protocols. Protocols and procedures to respond to and recover from de-energization events, which proactively prevent wildfires. Costs partially recovered. RSE is an estimate based on latest risk assessment. | NA | 0 | NA | NA | NA | 42000 | NA | NA | NA | 42000 | NA | NA | 84000
Other | Grid Operations & Operating Protocols | 7.3.6.6 | Stationed and on-call ignition prevention and suppression resources and services | Yes | Section 5.3 Table 5.3-1 |  |  |  | Other contact with object | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bear Valley Electric Service does not currently have stationed and on-call ignition prevention and suppression resources and services not captured in existing initiatives. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Other | Data Governance | 7.3.7.1 | Centralized repository for data | Yes | Section 5.3 Table 5.3-1 |  |  | 7.3.7.1 | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | D. 19-08-027 | GRC | NA | NA | Centralized repository for data | NA | GIS Data Collection & Sharing. Maintain and share Geographic Information System (GIS) database on system infrastructure for asset management and planning with key stakeholders. | NA | 0 | NA | NA | NA | 46382.29 | NA | NA | NA | 46382.29 | NA | NA | 92764.58
Other | Data Governance | 7.3.7.2 | Collaborative research on utility ignition and/or wildfire | No | N/A | No | N/A |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Collaborative research on utility ignition and/or wildfire | NA | Bear Valley Electric Service does not have a specific wildfire mitigation data governance plan focused on collaborative research on utility ignition or wildfire at this time. The company generally collaborates with Mutual Aid Partners and first responders to develop protocols, procedures, and communication plans to prevent, manage, and respond to utility ignition or wildfire. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Other | Data Governance | 7.3.7.3 | Documentation and disclosure of wildfire-related data and algorithms | No | N/A | Exploring Possibility | Dependent on timeline to execute Data Governance and GIS modeling enhancements |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Documentation and disclosure of wildfire-related data and algorithms | NA | Bear Valley Electric Service does not have a specific data governance wildfire mitigation program focused on documentation and disclosure of wildfire-related data and algorithms that maps to the tracking and level of detail requested in this table at this time. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Other | Data Governance | 7.3.7.4 | Tracking and analysis of near miss data | Yes | Section 5.3 Table 5.3-1 Section 7.3.2.9(1)D |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Tracking and analysis of near miss data | NA | Bear Valley Electric Service does not have a specific wildfire mitigation data governance initiative focused on tracking and analysis of near-miss data that maps to the tracking and level of detail requested in this table at this time but is in the process of enhancing its GIS data modeling capabilities. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Other | Resource Allocation Methodology | 7.3.8.1 | Allocation methodology development and application | Yes | Section 5.4; Section 7.3.2.8 |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Allocation methodology development and application | NA | BVES does not have a specific program allocated to this inititative category | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Other | Resource Allocation Methodology | 7.3.8.2 | Risk reduction scenario development and analysis | No | Section 4.5.1; Section 5.4 | Yes | Q2 2021 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Risk reduction scenario development and analysis | NA | N/A - While BVES is committed to the continued development and improvement of the company’s risk-based decision making framework, many of the elements requested in this filing may not be applicable to Bear Valley Electric Service, specifically many of the components requested in this section. Bear Valley Electric Service cannot provide information regarding BVES's wildifre mitigation resouce allocation methodology focused on risk spend efficiency analysis to the level of tracking and detail requested in this table at this time. At the guidance of the Wildfire Safety Division of the California Public Utilities Commission, these elements are marked “N/A" to indicate "does not apply" or "not applicable," with supplementary explanations where applicable througout the company's filing. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Other | Resource Allocation Methodology | 7.3.8.3 | Risk spend efficiency analysis | Yes | Section 4.2 (Figure 4.2-3) Section 4.5 |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Risk spend efficiency analysis | NA | N/A - While BVES is committed to the continued development and improvement of the company’s risk-based decision making framework, many of the elements requested in this filing may not be applicable to Bear Valley Electric Service, specifically many of the components requested in this section. Bear Valley Electric Service cannot provide information regarding BVES's wildifre mitigation resouce allocation methodology focused on risk spend efficiency analysis to the level of tracking and detail requested in this table at this time. At the guidance of the Wildfire Safety Division of the California Public Utilities Commission, these elements are marked “N/A" to indicate "does not apply" or "not applicable," with supplementary explanations where applicable througout the company's filing. The risk modeling process will begin in 2021 for enhanced predictive tools to influence the 2023 WMP | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Other | Emergency Planning & Preparedness | 7.3.9.1 | Adequate and trained workforce for service restoration | Yes | Section 5.4; Section 7.3.2.8 |  |  |  | NA | NA | NA | NA | NA | NA | NA | GRC | NA | In Compliance | GO 166 | Adequate and trained workforce for service restoration | NA | BVES does not have a specific program allocated to this inititative category | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Other | Emergency Planning & Preparedness | 7.3.9.2 | Community outreach, public awareness, and communications efforts | Yes | Under the Emergency Preparedness & Response Plan, Section 7.3.2.9, and in Appendix B. |  |  | 7.3.9.2; 7.3.10.1 | Other contact with object | NA | NA | NA | NA | NA | NA | GRC | NA | In Compliance | GO 167 | Customer support in emergencies | NA | BVES will be enhancing its communications and notification plans across multiple customer groups and stakeholder continuing in 2021 | 0 | 44791 | NA | NA | 0 | 15000 | NA | NA | 0 | 18000 | NA | NA | 77791
Other | Emergency Planning & Preparedness | 7.3.9.3 | Customer support in emergencies | Yes | Under the Emergency Preparedness & Response Plan, Section 7.3.2.9, and in Appendix B. |  |  | 7.3.9.3; 7.3.9.4; 7.3.9.5; 7.3.9.6 |  | NA | NA | NA | NA | NA | NA | GRC | NA | In Compliance | R. 18-12-005 | Customer support in emergencies | NA | BVES does not have a specific program allocated to this inititative category | NA | NA | NA | NA | 0 | 10000 | NA | NA | 0 | 10000 | NA | NA | 20000
Other | Emergency Planning & Preparedness | 7.3.9.4 | Disaster and emergency preparedness plan | Yes | Under the Emergency Preparedness & Response Plan, Section 7.3.2.9, and in Appendix B. |  |  |  | Other contact with object | Wire-to-wire contact | NA | NA | NA | NA | NA | D. 19-08-027 | NA | In Compliance | GO 166 | Disaster and emergency preparedness plan | NA | Emergency Reporting & Procedures. Protocols and procedures for staff to respond to faults, emergencies, outages, dissaster events (such as earthquake, wildfire, etc.), etc. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Other | Emergency Planning & Preparedness | 7.3.9.5 | Preparedness and planning for service restoration | Yes | Section 8.2, and Appendix A |  |  | 7.3.9.3; 7.3.9.4; 7.3.9.5; 7.3.9.6 | NA | NA | NA | NA | NA | NA | NA | D. 19-08-027 | CEMA, if applicable | In Compliance | GO 166 | Preparedness and planning for service restoration | NA | Post-Incident Recovery, Restoration & Remediation. Protocols and procedures to respond to and recover from any wildfire or related emergency events. | 0 | 2885 | NA | NA | 0 | 5000 | NA | NA | 0 | 5000 | NA | NA | 12885
Other | Emergency Planning & Preparedness | 7.3.9.6 | Protocols in place to learn from wildfire events | Yes | Under the Emergency Preparedness & Response Plan, Section 7.3.2.9, and in Appendix B. |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Protocols in place to learn from wildfire events | NA | Bear Valley Electric Service leverages the protocols included in the company’s Emergency Preparedness and Response Plan to learn from wildfire events in the same manner BVES learns from any emergency event. Therefore, Bear Valley Electric Service does not have specific protocols in place to learn from wildfire events that are not already covered in a previous program. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.1 | Community engagement | Yes | Section 7.3.2.10 |  |  | 7.3.9.2; 7.3.10.1 | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | NA | NA | Community engagement | NA | Bear Valley Electric Service does not have a community engagement program specific to wildfire mitigation at this time. BVES values community engagement as a wildfire risk mitigation strategy and has incorporated community engagement as a component of its overall Emergency Preparedness and Response Programs. BVES will be enhancing its communications and notification plans across multiple customer groups and stakeholder continuing in 2021 | NA | NA | NA | NA | 0 | 8000 | NA | NA | 0 | 8000 | NA | NA | 16000
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.2 | Cooperation and best practice sharing with agencies outside CA | No | N/A | Exploring Possibility | To be determined |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Cooperation and best practice sharing with agencies outside CA | NA | This is not a specifically budgeted program. This is a System Wide Initiative that targets all ignition probabilty drivers. As a System Wide Initiative, this initiative does not have a specified risk reduction or a risk spend efficiency. BVES' effort reduces the risk of escalation through support of accelerated restoration. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.3 | Cooperation with suppression agencies | No | N/A | Exploring Possibility | Q1 2022 |  | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | NA | NA | Cooperation with suppression agencies | NA | During emergency situations, Bear Valley Electric Service's [emergency management group] communicates and collaborates with federal and state emergency responders and mutual assistance groups, including fire suppression agencies. The emergency manager has contact information for [state, county and tribal emergency managers, the state’s Emergency Operations Center Emergency Support Functions (ESF) personnel, and the Geographic Area Coordination Centers dispatch centers for fire-related emergency response. ] | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.4 | Forest service and fuel reduction cooperation and joint roadmap | No | N/A | Exploring Possibility | Q1 2022 |  | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | NA | NA | Forest service and fuel reduction cooperation and joint roadmap | NA | While collaboration such as this is critical to the overall reduction of wildfire risk in the state of CA, Bear Valley Electric Service does not have program dedicated to cooperation with the forest service and fuel reduction and the development of a joint roadmap specific to this Wildfire Mitigation Plan. BVES views these efforts on an as-needed basis and incorporates additional efforts to manage community environments within other programs, such as those included in the company’s overall vegetation management and inspections programs. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
43356999.57